{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":2496,"n_cols":10,"rows_kept":2496,"cut":false,"hidden":false,"merged":[]}
["dom_code","dom_libelle","fame_code","fame_libelle","game_code","game_libelle","fapr_consignes","fapr_contenu","fapr_dureepres","fapr_dureejour"]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","Opération réalisée par un prestataire:\r\r[...] Contrôle de l'intensité absorbée et comparaison par rapport à l'intensité nominale constructeur",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle de l'isolement du compresseur et l'équipotentialité des masses",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle du fonctionnement de l'assécheur",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Dépoussiérage du condenseur de l'assécheur thermodynamique",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle des électrovannes de purge de l'assécheur (Réglage selon besoin)",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Nettoyage évacuation des condensats",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle des pressostats maxi et mini",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle des raccordements et des connexions électriques (boite à bornes du moteur)",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle du calibrage des fusibles et du réglage de la protection thermique",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle de la courroie",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle de l'état du filtre d'aspiration et remplacement si nécessaire",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Changement des clapets d'aspiration (selon besoin ou nombre d'heures)",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Vidange de l'huile (selon besoin ou nombre d'heures ) (Déchet DIS)",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Changement des filtres d'huile (selon besoin ou nombre d'heures ) (Déchet DIS)",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","[...] Contrôle de la date d'épreuve du réservoir.",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO6M","Production d'air comprimé"," ","      - Dernière épreuve: ..../…./20…",4,5]
["ACO","Air Comprimé","ACO","Production d'air comprimé","ACO1A","CR reservoir sous pression ","Purge du réseau avant toute intervention","[...]Contrôle reglementaire reservoir sous pression d'air",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Contrôle du fonctionnement général ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Contrôle de l' intensité absorbée et de l'isolement électrique ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Contrôle de l&#146;étanchéité des circuits frigorifiques ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Essai des pressostats HP/BP ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Essai du thermostat antigel et du pressostat huile ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Contrôle de l&#146;état du ventilateur et de la  batterie ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Contrôle du bon écoulement des eaux de condensation ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Resserrage des connexions électriques ",2,5]
["ACO","Air Comprimé","ASA","Assécheur d'air","ASA6M","Assécheur d'air"," ","[...] Nettoyage du ventilateur et de la batterie",2,5]
["ADM","Administration site","ACL","Auto contrôle des locaux"]
["ADM","Administration site","ASS-STCL","Assistance ST Client"]
["ADM","Administration site","FORM","Formation"]
["ADM","Administration site","REUN","Réunion"]
["CFA","Electricité - Courants faible","AUT","Autocommutateur","AUT1A","Autocommutateur"," ","Accompagnement du prestataire",1,5]
["CFA","Electricité - Courants faible","DFF","Détécteur de fluide frigo fixe"]
["CFA","Electricité - Courants faible","DIG","Digicode","DIG1A","Digicode"," ","[...] Contrôle de la fixation du boîtier ",1,5]
["CFA","Electricité - Courants faible","DIG","Digicode","DIG1A","Digicode"," ","[...] Contrôle des lignes et des impédances ",1,5]
["CFA","Electricité - Courants faible","DIG","Digicode","DIG1A","Digicode"," ","[...] Contrôle du fonctionnement de la gâche électrique ",1,5]
["CFA","Electricité - Courants faible","DIG","Digicode","DIG1A","Digicode"," ","[...] Essai de l'installation",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1A","GTC"," ","Accompagnement du prestataire",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Analyse des informations au fil de l’eau et déclenchement des interventions ",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Vérification des points de consignes ",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Edition des journaux d’alarmes, des analyses et des relevés sous tendance ",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Optimisation du fonctionnement des installations par téléréglage ",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Modification des programmes horaires ",1,5]
["CFA","Electricité - Courants faible","GTC","GTC","GTC1M","GTC"," ","[…] Création de points ponctuels, de synthèses ou de groupes de commande",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie",null,"Contrôle des liaisons d'écoute",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie",null,"Contrôle des lignes et des impédances",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie",null,"Contrôle des lignes et des impédances",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie",null,"Essai de l’installation",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie"," ","[...] Contrôle des liaisons d'écoute",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie"," ","[...] Contrôle des connexions électriques",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie"," ","[...] Contrôle des lignes et des impédances",1,5]
["CFA","Electricité - Courants faible","INT","Interphonie","INT1A","Interphonie"," ","[...] Essai de l’installation",1,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Contrôle général de l'installation ",2,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Nettoyage et vérification des connexions ",2,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Vérification tension alimentation ",2,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Vérification des batteries et chargeurs ",2,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Contrôle ampli des hauts parleurs ",2,5]
["CFA","Electricité - Courants faible","SON","Sonorisation","SON6M","Sonorisation"," ","[...] Essais du système (Si possible)",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Essai Auto/Arrêt/Manu ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Essai arrêt d'urgence ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle de l'intensité et de l'équilibrage des phases ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle de la présence du schéma dans l'armoire électrique.Remise à jour du schéma si nécessaire (Schéma indispensable ) ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Essai des disjoncteurs différentiels ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Essai des reports et télécommandes GTB ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle cohérence des indicateurs de mesure en façade ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Suivi de la procédure de consignation  ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle du serrage des connexions (En fonction de la thermographie) ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle du calibrage des fusibles par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle du réglage des relais thermiques par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle des temporisations ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle du pouvoir coupe circuit des disjoncteurs par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle des liaisons équipotentielles ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle état des goulottes ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle état des presse-étoupes ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle fixation de l'armoire ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Nettoyage et dépoussiérage ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Suivi de la procédure de déconsignation ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," "," ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","Opération réalisée par un sous-traitant ",2,5]
["CFO","Electricité - Courants forts","ARM","Armoire électrotechnique","ARM1A","Armoire électrotechnique"," ","[...] Contrôle thermique infrarouge (si contractuel)",2,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Relevé du courant de charge ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Mesure de la tension de chaque élément ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Essai d'autonomie et mesure de la tension globale de décharge tout au long de l'essai ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Mesure par sondage de la tension de certains éléments pendant la décharge ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Contrôle de l'état du support ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Consignation de l'installation ",1,5]
["CFO","Electricité - Courants forts","BAT-ET","Batterie d'accu type étanches","BAT1A-ET","Batterie d'accu type \"étanche\""," ","[...] Nettoyage, graissage des bornes et vérification du serrage",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Relevé du courant de charge ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Mesure de la tension de chaque élément ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Test d'autonomie et mesure de la tension  globale de décharge tout au long de l'essai ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Mesure par sondage de la tension de certains éléments au cours de la décharge ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Contrôle de l'état des supports ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Contrôle au pèse acide de chaque élément ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Consignation de l'installation ",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT1A-OU","Batteries d'accu type \"ouvert\""," ","[...] Nettoyage et graissage des bornes",1,5]
["CFO","Electricité - Courants forts","BAT-OU","Batteries d'accu type ouvert","BAT3M-OU","Batteries d'accu type \"ouvert\""," ","[...] Contrôle du niveau de l'électrolyte, appoint éventuel",1,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES1M","Bloc d'Éclairage de sécurité"," ","[...] Contrôle du bon fonctionnement en cas de défaillance de la source normale",0.02,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES6M","Bloc d'Éclairage de sécurité"," ","[...] Essai de la commande de mise au repos ",0.05,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES6M","Bloc d'Éclairage de sécurité"," ","[...] Contrôle de l’autonomie (1 heure) ",0.05,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES6M","Bloc d'Éclairage de sécurité"," ","[...] Contrôle de la fixation des blocs ",0.05,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES6M","Bloc d'Éclairage de sécurité"," ","[...] Remplacement des pictogrammes endommagés ou périmés ",0.05,5]
["CFO","Electricité - Courants forts","BES","Bloc d'Éclairage de sécurité","BES6M","Bloc d'Éclairage de sécurité"," ","[...] Contrôle de la présence d'un stock minimum des lampes et accumulateurs",0.05,5]
["CFO","Electricité - Courants forts","CAN","Canalis","CAN1A","Canalis"," ","[...] Suivi de la procédure de consignation ",1,5]
["CFO","Electricité - Courants forts","CAN","Canalis","CAN1A","Canalis"," ","[...] Contrôle de l'isolement électrique ",1,5]
["CFO","Electricité - Courants forts","CAN","Canalis","CAN1A","Canalis"," ","[...] Contrôle du verrouillage et organes de manoeuvre ",1,5]
["CFO","Electricité - Courants forts","CAN","Canalis","CAN1A","Canalis"," ","[...] Contrôle du serrage des connexions électriques ",1,5]
["CFO","Electricité - Courants forts","CAN","Canalis","CAN1A","Canalis"," ","[...] Suivi de la procédure de déconsignation",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL1A","Cellule HT"," ","[...] Dépoussiérage des cellules ",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL1A","Cellule HT"," ","[...] Suivi de la procédure de consignation  ",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL1A","Cellule HT"," ","[...] Essai des reports GTB ",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL1A","Cellule HT"," ","[...] Suivi de la procédure de déconsignation  ",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL1A","Cellule HT"," ","[...] Nettoyage du local technique",1,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","Opérations effectuées par le Constructeur: ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," "," ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l'état général des cellules et des connexions ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle des circuits de mise à la terre ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle du bon état des contacts, absence d'échauffement, d'amorçage ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Nettoyage et graissage des contacts ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle du bon fonctionnement des tringleries, des interrupteurs, des sectionneurs ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle mécanique des déclencheurs à fusible ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l'efficacité du verrouillage HT ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle du niveau huile dans les disjoncteurs huile ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle visuel de l'état des tètes de câbles ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l&#146;état et de la fixation des chemins de câbles ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Graissage des articulations mécaniques ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l&#146;isolement ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l&#146;état des conducteurs de protection ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle du réglage des dispositifs de protection ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle du bon fonctionnement des organes de commande et des dispositifs de verrouillage mécanique ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Contrôle de l&#146;alimentation auxiliaire et essai de décharge ",2,5]
["CFO","Electricité - Courants forts","CEL","Cellule HT","CEL3A","Cellule HT"," ","[...] Remplacement des batteries auxiliaires selon fréquence préconisée par le constructeur",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Suivi de la procédure de consignation ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," "," ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","Pied de colonne: ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Contrôle du serrage des connexions du pied de colonne ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Nettoyage et dépoussiérage ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," "," ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","Coffrets de raccordement: ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Contrôle de l'embrochage des coffrets  ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Contrôle du serrage des connexions de dérivation  ",2,5]
["CFO","Electricité - Courants forts","COE","Colonne montante","COE1A","Colonne montante"," ","[...]  Suivi de la procédure de déconsignation",2,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle de la présence du schéma dans l'armoire électrique.Remise à jour du schéma si nécessaire ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Essai Auto/Arrêt/Manu ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Essai arrêt d'urgence ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Suivi de la procédure de consignation  ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle connexions et bruits et fixations des relais ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Essai des reports et télécommandes GTB ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle du serrage des connexions ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle du calibrage des fusibles par rapport au schéma ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle du réglage des relais thermiques par rapport au schéma ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle des temporisations ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle état des goulottes ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle état des presse-étoupes ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Contrôle fixation du coffret ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Nettoyage et dépoussiérage ",0.5,5]
["CFO","Electricité - Courants forts","COF","Coffret électrique","COF1A","Coffret électrique"," ","[...] Suivi de la procédure de déconsignation",0.5,5]
["CFO","Electricité - Courants forts","CON","Batteries de condensateurs","CON1A","Batteries de condensateurs"," ","[...] Contrôle de la disponibilité ",1.5,5]
["CFO","Electricité - Courants forts","CON","Batteries de condensateurs","CON1A","Batteries de condensateurs"," ","[...] Contrôle des connexions ",1.5,5]
["CFO","Electricité - Courants forts","CON","Batteries de condensateurs","CON1A","Batteries de condensateurs"," ","[...] Dépoussiérage, nettoyage ",1.5,5]
["CFO","Electricité - Courants forts","CON","Batteries de condensateurs","CON1A","Batteries de condensateurs"," ","[...] Contrôle de l'état des contacteurs ",1.5,5]
["CFO","Electricité - Courants forts","CON","Batteries de condensateurs","CON1A","Batteries de condensateurs"," ","[...] Contrôle de la régulation varmétrique",1.5,5]
["CFO","Electricité - Courants forts","CPT-EL","Compteur électrique"]
["CFO","Electricité - Courants forts","CR-CFO","Contrôle electrique","CR-CFO1A","Contrôle reglementaire CFO"," ","[&#133;] Opération sous traitée ",8,5]
["CFO","Electricité - Courants forts","CR-CFO","Contrôle electrique","CR-CFO1A","Contrôle reglementaire CFO"," ","[&#133;] Contrôle electrique",8,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle des connexions ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle de l'état du bac ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle du niveau d'eau et ajout si nécessaire ( eau distillée) ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle des performances: ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","         -Relevé Id/IN ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","         -Relevé du temps de démarrage et comparaison avec les caractéristiques plaquées ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle du ou des thermostat de sécurité ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Contrôle de l'interrupteur centrifuge ",2,5]
["CFO","Electricité - Courants forts","DEM-AO","Démarreur bac AOIP","DEM6M-AO","Démarreur bac AOIP"," ","[...] Renouvellement de l'électrolyte ( suivant prescriptions constructeur (5ans) ou suivant performances",2,5]
["CFO","Electricité - Courants forts","DEM-EL","Démarreur électronique","DEM6M-EL","Démarreur électronique"," ","[...] Dépoussiérage du démarreur ",1,5]
["CFO","Electricité - Courants forts","DEM-EL","Démarreur électronique","DEM6M-EL","Démarreur électronique"," ","[...] Contrôle et serrage des connexions ",1,5]
["CFO","Electricité - Courants forts","DEM-EL","Démarreur électronique","DEM6M-EL","Démarreur électronique"," ","[...] Contrôle de la ventilation de l'armoire et remplacement du filtre si nécéssaire",1,5]
["CFO","Electricité - Courants forts","ECL","Eclairage (Source lumineuse)","ECL1M","Eclairage (Source lumineuse)"," ","Contrôle général ",4,5]
["CFO","Electricité - Courants forts","ECL","Eclairage (Source lumineuse)","ECL1M","Eclairage (Source lumineuse)"," ","[...] Remplacement ponctuel des sources lumineuses défectueuses ",4,5]
["CFO","Electricité - Courants forts","ECL","Eclairage (Source lumineuse)","ECL1M","Eclairage (Source lumineuse)"," ","[...] Remplacement ponctuel interrupteurs et boutons poussoir défectueux",4,5]
["CFO","Electricité - Courants forts","ENS","Enseigne","ENS6M","Enseigne"," ","[...] Contrôle du bon fonctionnement de l'interrupteur crépusculaire ",2,5]
["CFO","Electricité - Courants forts","ENS","Enseigne","ENS6M","Enseigne"," ","[...] Contrôle de la programmation horaire ",2,5]
["CFO","Electricité - Courants forts","ENS","Enseigne","ENS6M","Enseigne"," ","[...] Contrôle de la coupure de proximité ",2,5]
["CFO","Electricité - Courants forts","ENS","Enseigne","ENS6M","Enseigne"," ","[...] Contrôle de l'état du câblage ",2,5]
["CFO","Electricité - Courants forts","ENS","Enseigne","ENS6M","Enseigne"," ","[...] Contrôle de la fixation de l'enseigne",2,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1M","Groupe électrogène"," ","Lorsque le groupe dessert les installations de sécurité:  ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1M","Groupe électrogène"," ","[...] Essai de démarrage automatique avec une charge minimale de 50% de la puissance du groupe pendant 30 mn",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Opérations effectuées par le Constructeur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Moteur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle niveaux eau BT+ mesure protection  [...] Contrôle niveaux eau HT+ mesure protection ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle niveau huile moteur                          [...] Relevés des anomalies sur moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Inspection visuelle des tuyauteries                 [...] Recherche de fuite surles différents circuits ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle du degré de protection en antigel      [...] Contrôle de l'additif de refroidissement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de l'état des durits                           [...] Contrôle de l'état des flexibles ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle démarreur électrique                        [...] Contrôle de l'électrovanne de démarrage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Alternateur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de l'isolement      [...] Desserrage des connexions et mesure ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle interne des parties visibles   [...] Contrôle du pont de diode ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle régulation de tension     [...] Contrôle refroidissement alternateur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Graissage des roulements     [...] Contrôle protections alternateur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle circuit de terre et masse      [...] Nettoyage extérieur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Accouplement: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle visuel ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Echangeur BT/HT: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle visuel des échangeurs      [...] Contrôle visuel des pompes ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Resserrage des connexions      [...] Contrôle de l'isolement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Rechauffage moteur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle réchauffage eau      [...] Contrôle des connexions ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle du thermostat de régulation      [...] Contrôle de l'intensité de réchauffage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la tension ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Echappement: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle visuel silencieux et tuyauteries [...] Contrôle absence de fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Purge du circuit en point bas si possible  ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Armoire électrique: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Relevé des compteurs horaires [...] Vérification de l'ensemble des connexions ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Vérifications des borniers de liaison [...] Nettoyage et dépoussiérage des appareils et armoires ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des temporisations et réglages [...] Contrôle des appareils de mesures ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des voyants [...] Remplacement des ampoules ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des commandes auxiliaires [...] Nettoyage des organes de puissance ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Nettoyage des organes de protection [...] Contrôle des schémas et doc technique ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Batteries de démarrage: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Mesure de la densité élément par élément [...] Contrôle des niveaux élément par élément ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de l'intensité de charge [...] Contrôle de la tension batterie ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la tension de floating [...] Contrôle des cosses batteries et nettoyage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Graissage cosses [...] Resserrage cosses ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Batteries armoire: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Mesure de la densité élément par élément [...] Contrôle des niveaux élément par élément ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de l'intensité de charge [...] Contrôle de la tension batterie ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la tension de floating [...] Contrôle des cosses batteries et nettoyage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Graissage cosses [...] Resserrage cosses ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Aérorefroidisseur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle visuel refroidissement [...] Contrôle de l'état des vases d'expansion ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle absence de fuite [...] Resserrage des connexions ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des moteurs électriques [...] Contrôle de l'isolement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des liaisons électriques ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Réservoir journalier: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle visuel du réservoir [...] Contrôle des indicateurs de lecture ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle pompe de relevage [...] Contrôle de l'électrovanne fuel ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la valve anti siphon [...] Contrôle des tuyauteries jusqu'au moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la vanne police et alarme  ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Cuve principale: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle lecture de la jauge [...] Contrôle absence alarme fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la vanne police [...] Contrôle du dispositif anti-fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des connexions électriques ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Ventilateur du local: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle moteur électrique [...] Contrôle des connexions moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de l'isolement [...] Contrôle de l'intensité moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la tension [...] Contrôle des volets motorisés ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle du thermostat du local ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Visite électrique - Essais: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais à vide des différents démarrages ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais et contrôle des arrêts d'urgence ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais des sécurités à partir des organes ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des reports d'informations ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des éléments électriques tension ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des éléments électriques intensité ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des éléments électriques fréquence ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des éléments électriques puissance ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des éléments électriques cos phi ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle tension régulateur de tension ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle intensité régulateur de tension ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle indicateur moteur pression d'huile ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle indicateur moteur température eau ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle indicateur moteur température huile ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle indicateur moteur température échappement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais du groupe en position essais ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais du groupe en position auto ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais du groupe en position manuel ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais du groupe en charge coupures EDF ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Essais couplage entre groupe ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle des échanges de puissance ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle transfert de charge sur groupe ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle transfert de charge sur réseau ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","[...] Contrôle de la mise en automatique",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Opérations effectuées par le Constructeur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Moteur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle niveaux eau BT+ mesure protection ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle niveaux eau HT+ mesure protection ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle niveau huile moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Relevés des anomalies sur moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Inspection visuelle des tuyauteries ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Recherche de fuite surles différents circuits ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Resserrage de la boulonnerie apparente ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Appoint ingrédient ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Graissage selon préconisation constructeur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle du degré de protection en antigel ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle de l'additif de refroidissement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des jeux de culbuteurset réglages ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle filtre à air ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle de l'état des durits ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle de l'état des flexibles ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle démarreur électrique ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Nettoyage du groupe ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des fumées si possible ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle plots de suspension ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Alternateur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Graissage des roulements ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle serrage alternateur sur moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle serrage alternateur sur châssis ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Accouplement: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle serrage accouplement ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Echangeur BT/HT: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle visuel des échangeurs ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle visuel des vannes et manœuvres ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Purge de l'ensemble si possible ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Rechauffage moteur: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle réchauffage eau ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle température de réchauffage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Echappement: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle visuel silencieux et tuyauteries ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle absence de fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Purge du circuit en point bas si possible ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des fumées, si possible ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Armoire électrique: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Relevé des compteurs horaires ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Batteries de démarrage: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des niveaux élément par élément ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des cosses batteries et nettoyage ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Graissage cosses ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Réservoir journalier: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle visuel du réservoir ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle absence de fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des indicateurs de lecture ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des tuyauteries jusqu'au moteur ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle de la vanne police et alarme ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Cuve principale: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle lecture de la jauge ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle absence alarme fuite ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle de la vanne police ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Ventilateur du local: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des entrées d'air local ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle des sorties d'air local ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Contrôle, essais de l'ensemble ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," "," ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Visite électrique - Essais: ",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","[...] Essais en charge (avec accord client)",1,5]
["CFO","Electricité - Courants forts","GEL","Groupe électrogène","GEL15J","Contrôle GE"," ","Suivant l'arrété du 26 février 2003\n\n[...] Vérification du niveau d'huile\n[...] Vérification du niveau de combustibre\n[...] Vérification du niveau d'eau\n[...] Vérification du préchauffage",0.5,5]
["CFO","Electricité - Courants forts","GEL-VE","Groupe électrogène","GEL1A-VE","Groupe électrogène"," ","Opérations effectuées par le Constructeur:\n\nMoteur:\n[...] Contrôle niveaux eau BT+ mesure protection  [...] Contrôle niveaux eau HT+ mesure protection\n[...] Contrôle niveau huile moteur                          [...] Relevés des anomalies sur moteur\n[...] Inspection visuelle des tuyauteries                 [...] Recherche de fuite surles différents circuits\n[...] Contrôle du degré de protection en antigel      [...] Contrôle de l'additif de refroidissement\n[...] Contrôle de l'état des durits                           [...] Contrôle de l'état des flexibles\n[...] Contrôle démarreur électrique                        [...] Contrôle de l'électrovanne de démarrage\n\nAlternateur:\n[...] Contrôle de l'isolement      [...] Desserrage des connexions et mesure\n[...] Contrôle interne des parties visibles   [...] Contrôle du pont de diode\n[...] Contrôle régulation de tension     [...] Contrôle refroidissement alternateur\n[...] Graissage des roulements     [...] Contrôle protections alternateur\n[...] Contrôle circuit de terre et masse      [...] Nettoyage extérieur\n\nAccouplement:\n[...] Contrôle visuel\n\nEchangeur BT/HT:\n[...] Contrôle visuel des échangeurs      [...] Contrôle visuel des pompes\n[...] Resserrage des connexions      [...] Contrôle de l'isolement\n\nRechauffage moteur:\n[...] Contrôle réchauffage eau      [...] Contrôle des connexions\n[...] Contrôle du thermostat de régulation      [...] Contrôle de l'intensité de réchauffage\n[...] Contrôle de la tension\n\nEchappement:\n[...] Contrôle visuel silencieux et tuyauteries [...] Contrôle absence de fuite\n[...] Purge du circuit en point bas si possible \n\nArmoire électrique:\n[...] Relevé des compteurs horaires [...] Vérification de l'ensemble des connexions\n[...] Vérifications des borniers de liaison [...] Nettoyage et dépoussiérage des appareils et armoires\n[...] Contrôle des temporisations et réglages [...] Contrôle des appareils de mesures\n[...] Contrôle des voyants [...] Remplacement des ampoules\n[...] Contrôle des commandes auxiliaires [...] Nettoyage des organes de puissance\n[...] Nettoyage des organes de protection [...] Contrôle des schémas et doc technique\n\nBatteries de démarrage:\n[...] Mesure de la densité élément par élément [...] Contrôle des niveaux élément par élément\n[...] Contrôle de l'intensité de charge [...] Contrôle de la tension batterie\n[...] Contrôle de la tension de floating [...] Contrôle des cosses batteries et nettoyage\n[...] Graissage cosses [...] Resserrage cosses\n\nBatteries armoire:\n[...] Mesure de la densité élément par élément [...] Contrôle des niveaux élément par élément\n[...] Contrôle de l'intensité de charge [...] Contrôle de la tension batterie\n[...] Contrôle de la tension de floating [...] Contrôle des cosses batteries et nettoyage\n[...] Graissage cosses [...] Resserrage cosses\n\nAérorefroidisseur:\n[...] Contrôle visuel refroidissement [...] Contrôle de l'état des vases d'expansion\n[...] Contrôle absence de fuite [...] Resserrage des connexions\n[...] Contrôle des moteurs électriques [...] Contrôle de l'isolement\n[...] Contrôle des liaisons électriques\n\n\nRéservoir journalier:\n[...] Contrôle visuel du réservoir [...] Contrôle des indicateurs de lecture\n[...] Contrôle pompe de relevage [...] Contrôle de l'électrovanne fuel\n[...] Contrôle de la valve anti siphon [...] Contrôle des tuyauteries jusqu'au moteur\n[...] Contrôle de la vanne police et alarme \n\nCuve principale:\n[...] Contrôle lecture de la jauge [...] Contrôle absence alarme fuite\n[...] Contrôle de la vanne police [...] Contrôle du dispositif anti-fuite\n[...] Contrôle des connexions électriques\n\nVentilateur du local:\n[...] Contrôle moteur électrique [...] Contrôle des connexions moteur\n[...] Contrôle de l'isolement [...] Contrôle de l'intensité moteur\n[...] Contrôle de la tension [...] Contrôle des volets motorisés\n[...] Contrôle du thermostat du local\n\nVisite électrique - Essais:\n[...] Essais à vide des différents démarrages\n[...] Essais et contrôle des arrêts d'urgence\n[...] Essais des sécurités à partir des organes\n[...] Contrôle des reports d'informations\n[...] Contrôle des éléments électriques tension\n[...] Contrôle des éléments électriques intensité\n[...] Contrôle des éléments électriques fréquence\n[...] Contrôle des éléments électriques puissance\n[...] Contrôle des éléments électriques cos phi\n[...] Contrôle tension régulateur de tension\n[...] Contrôle intensité régulateur de tension\n[...] Contrôle indicateur moteur pression d'huile\n[...] Contrôle indicateur moteur température eau\n[...] Contrôle indicateur moteur température huile\n[...] Contrôle indicateur moteur température échappement\n[...] Essais du groupe en position essais\n[...] Essais du groupe en position auto\n[...] Essais du groupe en position manuel\n[...] Essais du groupe en charge coupures EDF\n[...] Essais couplage entre groupe\n[...] Contrôle des échanges de puissance\n[...] Contrôle transfert de charge sur groupe\n[...] Contrôle transfert de charge sur réseau\n[...] Contrôle de la mise en automatique",1,5]
["CFO","Electricité - Courants forts","GEL-VM","Groupe électrogène","GEL6M-VM","Groupe électrogène"," ","Opérations effectuées par le Constructeur:\n\nMoteur:\n[...] Contrôle niveaux eau BT+ mesure protection\n[...] Contrôle niveaux eau HT+ mesure protection\n[...] Contrôle niveau huile moteur\n[...] Relevés des anomalies sur moteur\n[...] Inspection visuelle des tuyauteries\n[...] Recherche de fuite surles différents circuits\n[...] Resserrage de la boulonnerie apparente\n[...] Appoint ingrédient\n[...] Graissage selon préconisation constructeur\n[...] Contrôle du degré de protection en antigel\n[...] Contrôle de l'additif de refroidissement\n[...] Contrôle des jeux de culbuteurset réglages\n[...] Contrôle filtre à air\n[...] Contrôle de l'état des durits\n[...] Contrôle de l'état des flexibles\n[...] Contrôle démarreur électrique\n[...] Nettoyage du groupe\n[...] Contrôle des fumées si possible\n[...] Contrôle plots de suspension\n\nAlternateur:\n[...] Graissage des roulements\n[...] Contrôle serrage alternateur sur moteur\n[...] Contrôle serrage alternateur sur châssis\n\nAccouplement:\n[...] Contrôle serrage accouplement\n\nEchangeur BT/HT:\n[...] Contrôle visuel des échangeurs\n[...] Contrôle visuel des vannes et man&#156;uvres\n[...] Purge de l'ensemble si possible\n\nRechauffage moteur:\n[...] Contrôle réchauffage eau\n[...] Contrôle température de réchauffage\n\nEchappement:\n[...] Contrôle visuel silencieux et tuyauteries\n[...] Contrôle absence de fuite\n[...] Purge du circuit en point bas si possible\n[...] Contrôle des fumées, si possible\n\nArmoire électrique:\n[...] Relevé des compteurs horaires\n\nBatteries de démarrage:\n[...] Contrôle des niveaux élément par élément\n[...] Contrôle des cosses batteries et nettoyage\n[...] Graissage cosses\n\nRéservoir journalier:\n[...] Contrôle visuel du réservoir\n[...] Contrôle absence de fuite\n[...] Contrôle des indicateurs de lecture\n[...] Contrôle des tuyauteries jusqu'au moteur\n[...] Contrôle de la vanne police et alarme\n\nCuve principale:\n[...] Contrôle lecture de la jauge\n[...] Contrôle absence alarme fuite\n[...] Contrôle de la vanne police\n\nVentilateur du local:\n[...] Contrôle des entrées d'air local\n[...] Contrôle des sorties d'air local\n[...] Contrôle, essais de l'ensemble\n\n\nVisite électrique - Essais:\n[...] Essais en charge (avec accord client)",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Essai des commutateurs de sélection S1/S2 ",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Essai de l'inversion des sources ",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Contrôle de l'intensité générale et de la tension sur chaque phase ",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Contrôle de l'équilibrage des phases ",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Contrôle du réglage des temporisations ",1,5]
["CFO","Electricité - Courants forts","INV","Inverseur de source","INV1A","Inverseur de source"," ","[...] Contrôle du relayage général (bruit, fixation&#133;)",1,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","Opérations effectuées par le Prestataire: ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","Contrôle Logiciel:   ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Vérification des paramètres de programmation des microprocesseurs, remise à niveau si nécessaire ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Etalonnage de la chaîne de mesure ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," "," ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","Contrôle batterie: ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Essai d’autonomie avec la charge réelle ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle de la tension des monoblocs Batterie si accessible ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle de la température du local Batterie ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Compensation de la tension de floating en fonction de la température ambiante ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," "," ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","Carte électronique: ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure à vide et en charge du courant par phase en amont du redresseur ( contrôle et équilibrage ) ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure à vide et en charge de la tension de floating ( tension continue ), ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure des tensions d’alimentation du pont à thyristors ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle des alarmes et des sécurités ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle électronique ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle des alimentations électroniques ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle de la ventilation ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," "," ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","Onduleur: ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure à vide et en charge des courants du filtre de sorties ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure à vide et en charge des tensions en sortie de l’onduleur ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure de la charge sur onduleur  ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Essai d’auto-alimentation et mesure de la fréquence propre ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle des alarmes et des sécurités ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle de l’électronique de l’onduleur ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle de la ventilation et contrôle du bon fonctionnement de l’écran clavier. ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," "," ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","By-pass: ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure des tensions réseau ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle des alarmes et des sécurités ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Essai de By-pass par commande écran clavier ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Contrôle électronique de la logique By-pass ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1A","Onduleur"," ","[...] Mesure de la charge sur le réseau ",4,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1M","Onduleur"," ","[...] Contrôle de la ventilation et remplacement du filtre si nécéssaire ",1,5]
["CFO","Electricité - Courants forts","OND","Onduleur","OND1M","Onduleur"," ","[...] Contrôle état des batterie, absence de fuite.",1,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","Opérations effectuées par le Prestataire: ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","Capteurs: ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de l'état mécanique : solidité, tenue de la fixation, degré d'oxydation, effilement de la pointe ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de la continuité électrique au point de raccordement avec le conducteur de toiture ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle visuel d'une mesure de conformité à l'ohmètre ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," "," ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","Circuit de toiture: ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle visuel de l'état mécanique et de la continuité du conducteur  ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de la continuité électrique aux points de jonction éventuels  ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de l'état et de la solidité des fixations ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," "," ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","Circuit de descente: ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle visuel de l'état mécanique et de la continuité du conducteur  ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de la continuité électrique aux points de jonction éventuels  ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de l'état et de la solidité des fixations ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Vérification du joint de contrôle si celui-ci existe ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Contrôle de l'état de la gaine de protection mécanique ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," "," ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","Prise de terre: ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Mesure de la résistance ohmique, celle-ci devant être inférieure à 10 ohms  ",4,5]
["CFO","Electricité - Courants forts","PAR","Paratonnerre dispo d'amorçage","PAR1A","Paratonnerre à dispos amorçage"," ","[...] Evaluation de la forme et de la constitution",4,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","Parking -2 : ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des luminaires ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des luminaires si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des interrupteurs ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des interrupteurs si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","Parking -1 : ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des luminaires ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des luminaires si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des interrupteurs ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des interrupteurs si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","Rez-de-chaussée : ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des luminaires ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des luminaires si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des interrupteurs ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des interrupteurs si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","Locaux techniques : ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses"," ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des luminaires ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des luminaires si défectueux ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Vérification du bon fonctionnement des interrupteurs ",2,5]
["CFO","Electricité - Courants forts","RECL","Ronde éclairage","ECL1M","Eclairage (Source lumineuse)","Utilisation obligatoire de Gazelle pour le remplacement des sources Lumineuses","[...] Remplacement des interrupteurs si défectueux",2,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Essai Auto/Arrêt/Manu ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Essai arrêt d'urgence ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle de l'intensité et de l'équilibrage des phases ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle de la présence du schéma dans l'armoire électrique.Remise à jour du schéma si nécessaire (Schéma indispensable ) ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Essai des disjoncteurs différentiels ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Essai des reports et télécommandes GTB ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle cohérence des indicateurs de mesure en façade ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Suivi de la procédure de consignation  ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle du serrage des connexions (En fonction de la thermographie) ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle du calibrage des fusibles par rapport au schéma ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle du pouvoir coupe circuit des disjoncteurs par rapport au schéma ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle des liaisons équipotentielles ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle état des goulottes ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle état des presse-étoupes ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle fixation de l'armoire ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Nettoyage et dépoussiérage ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Suivi de la procédure de déconsignation ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," "," ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","Opération réalisée par un sous-traitant ",1,5]
["CFO","Electricité - Courants forts","TAB","Tableau  électrique d'étage","TAB1A","Tableau  électrique d'étage"," ","[...] Contrôle thermique infrarouge (si contractuel)",1,5]
["CFO","Electricité - Courants forts","TD","Tableau Divisionaire"]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle fonctionnement éclairage armoire ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle état et fixation des chemins de câbles ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Suivi de la procédure de consignation  ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Nettoyage et dépoussiérage ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Graissage des articulations et contacts mécaniques ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du serrage des jeux de barre (en fonction de la thermographie) ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du serrage des connexions (en fonction de la thermographie) ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle connexions, bruits et fixations des relais ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle de la présence du schéma ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du pouvoir coupe-circuit des disjoncteurs par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du réglage des relais thermiques par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du réglage des relais magnétiques par rapport au schéma ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle des liaisons équipotentielles ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle de l’alimentation auxiliaire et essai de décharge ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Remplacement des batteries auxiliaires (tous les 3 à 5 ans) ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle de la date du dernier remplacement ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Sauvegarde des programmes automates ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle du réglage des disjoncteurs différentiels et essais ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Essai des reports et commandes GTB ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Remise à jour du schéma si nécessaire ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Suivi de la procédure de déconsignation  ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle cohérence des indicateurs de mesure en façade ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," "," ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","Opération réalisée par un sous-traitant ",2,5]
["CFO","Electricité - Courants forts","TGB","TGBT","TGB1A","TGBT"," ","[...] Contrôle thermographie infrarouge ",2,5]
["CFO","Electricité - Courants forts","THERMO","Contrôle Thermographie","THE1A","Contrôle Thermographie"," ","[...] Vérification thermographie des installations électriques",8,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle de la présence et de l'état du dispositif de rétention sous le transformateur  ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle de la présence de l'étiquette jaune  fixée sur l'appareil portant la mention : \"Cet appareil contient des PCB qui pourraient contaminer l'environnement et dont l'élimination est réglementée\" ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Suivi de la procédure de consignation  ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle de l'état et de la fixation des chemins de câbles ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle du serrage des connexions ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle du circuit de la mise à la terre en fonction du régime de neutre ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Dépoussiérage du transformateur ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Test de la protection thermique du transformateur ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Contrôle de la date du dernier prélèvement ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Essai des reports GTB ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Suivi de la procédure de déconsignation  ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH1A","Transformateur à Huile"," ","[...] Nettoyage du local technique ",2,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH3A","Transformateur à Huile"," ","Opérations effectuées par le Prestataire: ",1,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH3A","Transformateur à Huile"," ","Prélèvement du diélectrique pour analyse ",1,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH3A","Transformateur à Huile"," "," ",1,5]
["CFO","Electricité - Courants forts","TRH","Transformateur à Huile","TRH3A","Transformateur à Huile"," ","NOTA.: Fréquence préconisée par le constructeur 2 à 5 ans",1,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle de la présence et de l'état du dispositif de rétention sous le transformateur  ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle de la présence de l'étiquette jaune  fixée sur l'appareil portant la mention : \"Cet appareil contient des PCB qui pourraient contaminer l'environnement et dont l'élimination est réglementée\" ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Suivi de la procédure de consignation  ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle de l'état et de la fixation des chemins de câbles ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle du serrage des connexions ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle du circuit de la mise à la terre en fonction du régime de neutre ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Dépoussiérage du transformateur ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Test de la protection thermique du transformateur ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Contrôle de la date du dernier prélèvement ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Essai des reports GTB ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Suivi de la procédure de déconsignation  ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP1A","Transformateur PCB"," ","[...] Nettoyage du local technique ",2,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP3A","Transformateur PCB"," ","Opérations effectuées par le Prestataire: ",1,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP3A","Transformateur PCB"," ","Prélèvement du diélectrique pour analyse ",1,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP3A","Transformateur PCB"," "," ",1,5]
["CFO","Electricité - Courants forts","TRP","Transformateur PCB","TRP3A","Transformateur PCB"," ","NOTA.: Fréquence préconisée par le constructeur 2 à 5 ans",1,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Suivi de la procédure de consignation ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Contrôle  de l'état et de la fixation des chemins de câbles ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Contrôle des protections disjoncteurs ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Contrôle du serrage des connexions, de l'absence d'échauffements, d'amorçage ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Contrôle du circuit de la mise à la terre en fonction du régime de neutre ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Dépoussiérage du transformateur ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Contrôle de la consigne du thermostat d'alarme et du thermostat de déclenchement selon préconisations constructeur  ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Essai des reports GTB ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Suivi de la procédure de déconsignation ",2,5]
["CFO","Electricité - Courants forts","TRS","Transformateur sec","TRS1A","Transformateur sec"," ","[...] Nettoyage du local technique",2,5]
["CFO","Electricité - Courants forts","VAR","Variateur de vitesse","VAR1A","Variateur de vitesse"," ","[...] Dépoussiérage du variateur ",2,5]
["CFO","Electricité - Courants forts","VAR","Variateur de vitesse","VAR1A","Variateur de vitesse"," ","[...] Contrôle et serrage des connexions ",2,5]
["CFO","Electricité - Courants forts","VAR","Variateur de vitesse","VAR1A","Variateur de vitesse"," ","[...] Vérification des paramètres de commande et de sécurité ",2,5]
["CFO","Electricité - Courants forts","VAR","Variateur de vitesse","VAR1A","Variateur de vitesse"," ","[...] Contrôle du signal d'entrée et de sortie ",2,5]
["CFO","Electricité - Courants forts","VAR","Variateur de vitesse","VAR1A","Variateur de vitesse"," ","[...] Contrôle de la ventilation de l'armoire et remplacement du filtre si nécéssaire",2,5]
["CUIS","Matériel de cuisine","BAL","Balance"]
["CUIS","Matériel de cuisine","BAM","Batteur mélangeur"]
["CUIS","Matériel de cuisine","BCO","Bahut congélateur"]
["CUIS","Matériel de cuisine","BMF-EL","Bain Marie Electrique"]
["CUIS","Matériel de cuisine","BMF-GA","Bain-marie gaz"]
["CUIS","Matériel de cuisine","BMM-EL","Bain-marie mobil électrique"]
["CUIS","Matériel de cuisine","CAB","Convoyeur à bande"]
["CUIS","Matériel de cuisine","CFA","Chauffe assiettes"]
["CUIS","Matériel de cuisine","CFR","Chambre froid. meubles réfrig."]
["CUIS","Matériel de cuisine","CLE","Coupe légumes"]
["CUIS","Matériel de cuisine","CMT","Chariot de maintien en temp."]
["CUIS","Matériel de cuisine","CRR","Cellule de refroidissement "]
["CUIS","Matériel de cuisine","CUT","Cutter"]
["CUIS","Matériel de cuisine","CVA-GA","Cuiseur vapeur GAZ"]
["CUIS","Matériel de cuisine","DEI","Destructeur d'insectes"]
["CUIS","Matériel de cuisine","DIVC","Divers Cuisine"]
["CUIS","Matériel de cuisine","DSI-OZ","DSI-OZ"]
["CUIS","Matériel de cuisine","EPL","Eplucheuse"]
["CUIS","Matériel de cuisine","ESS","Essoreuse"]
["CUIS","Matériel de cuisine","ETU","Etuve"]
["CUIS","Matériel de cuisine","EXA-AR","Extinction automatique  Argon"]
["CUIS","Matériel de cuisine","EXM","Extraction magnétique"]
["CUIS","Matériel de cuisine","FMA-EL","Four mixte élect. et air pulsé"]
["CUIS","Matériel de cuisine","FMA-GA","Four mixte gaz et air pulsé"]
["CUIS","Matériel de cuisine","FMO","Four micro-ondes"]
["CUIS","Matériel de cuisine","FON","Fontaines"]
["CUIS","Matériel de cuisine","FOU-EL","Fourneau électrique"]
["CUIS","Matériel de cuisine","FOU-GA","Fourneau gaz"]
["CUIS","Matériel de cuisine","FRI-EL","Friteuse électrique"]
["CUIS","Matériel de cuisine","FRI-GA","Friteuse gaz"]
["CUIS","Matériel de cuisine","FRT","Four de remise en température"]
["CUIS","Matériel de cuisine","GRI-EL","Grillade et snack électrique"]
["CUIS","Matériel de cuisine","GRI-GA","Grillade Gaz"]
["CUIS","Matériel de cuisine","HAC","Hachoir"]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT1S","Filtration Hottes"," ","Opération Sous traitée ",0.5,5]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT1S","Filtration Hottes"," "," ",0.5,5]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT1S","Filtration Hottes"," ","Remplacement des filtres des hottes",0.5,5]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT6M","Dégraissage des hottes"," ","Opération sous traitée ",1,5]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT6M","Dégraissage des hottes"," "," ",1,5]
["CUIS","Matériel de cuisine","HOT","Hottes","HOT6M","Dégraissage des hottes"," ","Dégraissage des hottes",1,5]
["CUIS","Matériel de cuisine","LAM","Laminoir"]
["CUIS","Matériel de cuisine","MAC","Machine à café"]
["CUIS","Matériel de cuisine","MAG","Machines à glaçons"]
["CUIS","Matériel de cuisine","MAS-EL","Marmite et sauteuse électrique"]
["CUIS","Matériel de cuisine","MAS-GA","Marmite et sauteuse gaz"]
["CUIS","Matériel de cuisine","MIX","Mixeur"]
["CUIS","Matériel de cuisine","MLV","Machine à laver "]
["CUIS","Matériel de cuisine","MMT","Meuble de maintien en temp."]
["CUIS","Matériel de cuisine","OUB","Ouvre boîtes"]
["CUIS","Matériel de cuisine","PCF-EL","Poly-cuiseur Frimax électrique"]
["CUIS","Matériel de cuisine","PCF-GA","Poly-cuiseur Frimax gaz"]
["CUIS","Matériel de cuisine","PLA-EL","Plaque électrique"]
["CUIS","Matériel de cuisine","PLA-GA","Plaque GAZ"]
["CUIS","Matériel de cuisine","RSF","Réserve à frites chauffante"]
["CUIS","Matériel de cuisine","SAL","Salamandre"]
["CUIS","Matériel de cuisine","SEPGRAISSE","Séparateur à graisse"]
["CUIS","Matériel de cuisine","STE","Armoire stérilisation couteaux"]
["CUIS","Matériel de cuisine","TRA","Trancheur"]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Essai des fonctions Auto/Arrêt/Manu ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la commande locale Chaud/Froid/Vitesse ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la programmation horaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Nettoyage général interne, externe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle des filtres et remplacement si nécessaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Manœuvre des vannes d'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Ventilateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la tension de l'alignement et de l'état des courroies ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Graissage des paliers moteurs et turbine ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'isolement et de l'intensité absorbée du moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du serrage de la boite à bornes moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la fixation de l'ensemble moteur ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'état des roulements moteur et ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Circuit frigorifique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle  des connexions plaque à borne moteur du compresseur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle des pressions HP/BP et de l'état anhydre du circuit ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle des pressostats de régulation HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle des pressostats de sécurité HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du voyant liquide ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du filtre déhydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'isolement et de l'intensité absorbée du ou des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'état des calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la charge frigorifique et  de l'étanchéité du circuit ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Nota.: Attention remplir le certificat de recherche de fuite annuelle ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Réseau évaporateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle évacuation condensats et nettoyage du bac ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle état de la batterie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Condensation à air: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle général du condenseur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'intensité absorbée du ou des ventilateurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de la protection électrique du condenseur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Nettoyage du condenseur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Nettoyage du ou des ventilateurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Batterie électrique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du fonctionnement  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'isolement et de l'intensité absorbée ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du thermostat de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Humidificateur vapeur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'intensité absorbée et de l'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle de l'étanchéité des conduits vapeur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle des électrodes et de la cuve ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","Régulation: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du serrage des connexions ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CA","Armoire Clim Autonome cond air","ACA6M-CA","Armoire Clim Autonome cond air"," ","[...] Contrôle du fonctionnement de la régulation (Points de consignes, paramètres de fonctionnement)",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Essai des fonctions Auto/Arrêt/Manu ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la commande locale Chaud/Froid/Vitesse ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la programmation horaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Nettoyage général interne, externe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle des filtres et remplacement si nécessaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Manœuvre des vannes d'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Ventilateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la tension de l'alignement et de l'état des courroies ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Graissage des paliers moteurs et turbine ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'isolement et de l'intensité absorbée du moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du serrage de la boite à bornes moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la fixation de l'ensemble moteur ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'état des roulements moteur et ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Circuit frigorifique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle  des connexions plaque à borne moteur du compresseur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle des pressions HP/BP et de l'état anhydre du circuit ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle des pressostats de régulation HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle des pressostats de sécurité HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du voyant liquide ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du filtre déhydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'isolement et de l'intensité absorbée du ou des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'état des calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la charge frigorifique et  de l'étanchéité du circuit ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Nota.: Attention remplir le certificat de recherche de fuite annuelle ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Réseau évaporateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle évacuation condensats et nettoyage du bac ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle état de la batterie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Condensation à eau: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la vanne pressostatique ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Vérification de l'étanchéité des joints et des flexibles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle vanne d'isolement et filtre à tamis ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du bon écoulement des eaux ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Relevé du compteur d'eau ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Batterie électrique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du fonctionnement  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'isolement et de l'intensité absorbée ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du thermostat de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Humidificateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du système d'alimentation automatique en eau ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Nettoyage du bac ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de la régulation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Humidificateur vapeur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'intensité absorbée et de l'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle de l'étanchéité des conduits vapeur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle des électrodes et de la cuve ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","Régulation: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du serrage des connexions ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACA-CE","Armoire Clim Autonome cond eau","ACA6M-CE","Armoire Clim Autonome cond eau"," ","[...] Contrôle du fonctionnement de la régulation (Points de consignes, paramètres de fonctionnement)",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Essai des fonctions Auto/Arrêt/Manu ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de la commande locale Chaud/Froid/Vitesse ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de la programmation horaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Nettoyage général interne, externe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle des filtres et remplacement si nécessaire ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Man&#156;uvre des vannes d'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Ventilateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de la tension de l'alignement et de l'état des courroies ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Graissage des paliers moteurs et turbine ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'isolement et de l'intensité absorbée du moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du serrage de la boite à bornes moteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de la fixation de l'ensemble moteur ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'état des roulements moteur et ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Réseau hydraulique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'étanchéité des vannes d'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'étanchéité et de l'état de la batterie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle évacuation condensats et nettoyage du bac ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'état du calorifuge ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Batterie électrique: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du fonctionnement  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'isolement et de l'intensité absorbée ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du thermostat de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Humidificateur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du système d'alimentation automatique en eau ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Nettoyage du bac ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de la régulation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Humidificateur vapeur: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'intensité absorbée et de l'isolement ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle de l'étanchéité des conduits vapeur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle des électrodes et de la cuve ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","Régulation: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du serrage des connexions ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ACE","Armoire de Clim à eau glacée","ACE6M","Armoire de Clim à eau glacée"," ","[...] Contrôle du fonctionnement de la régulation (Points de consignes, paramètres de fonctionnement)",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle du bon fonctionnement de la régulation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle du filtre et remplacement si nécessaire ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Dépoussiérage des batteries et du moto ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle de l'intensité et de l'isolement du moto ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","Batterie chaude: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Purge de l'air de la batterie ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle du fonctionnement de la régulation et des électrovannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle de la robinetterie d'isolement, man&#156;uvre des vannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle des presses étoupes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","Batterie électrique: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle de l'intensité batterie électrique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle des connexions électriques ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","AER","Aérotherme","AER6M","Aérotherme"," ","[...] Contrôle de l'état du calorifuge",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BAC","Réservoir et bâche à eau","BAC1A","Réservoir et bâche à eau"," ","[...] Vidange de la bâche ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BAC","Réservoir et bâche à eau","BAC1A","Réservoir et bâche à eau"," ","[...] Contrôle des différentes vannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BAC","Réservoir et bâche à eau","BAC1A","Réservoir et bâche à eau"," ","[...] Contrôle du flotteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BAC","Réservoir et bâche à eau","BAC1A","Réservoir et bâche à eau"," ","[...] Nettoyage de la bâche ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BAC","Réservoir et bâche à eau","BAC1A","Réservoir et bâche à eau"," ","[...] Contrôle remplissage par flotteur et surpresseur",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BALC","Ballon de stokage chaud"]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle de l'état général ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle et resserrage des connexions électriques ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle des débits d'air maxi et mini au manomètre différentiel ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle de l'état de la tringlerie (piston/registre) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle de l'état des raccordements aérauliques ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle de l'encrassement batterie et nettoyage si nécessaire ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle presse-étoupe vanne de régulation ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Vérification fonctionnelle de la régulation et servomoteur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Contrôle de l'état général (fuite d'air) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Man&#156;uvre des vannes d'isolement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BDV","Boite détente à débit variable","BDV1A","Boite détente à débit variable"," ","[...] Relevé des débits et pressions sur fiche",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","[...] Contrôle brûleur et analyse de la combustion (CO², CO,T°C fumées, indice de noircissement, rendement)  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","[...] Mise à jour du livret de chaufferie ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","NOTA.: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","Chaudière neuve (mise en service après le 13/03/00) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","  - Rendement : 89% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","Chaudière existante ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","  - Entre 400 et 2000kW = 85% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","  - Entre 2000 et 10 000kW = 86% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU3M-FU","Brûleur fuel "," ","  - Entre 10 000 et 50 000kW =87%  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état et man&#156;uvre des vannes ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle débit et des sondes de températures départ/retour ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle et essai des sécurités ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état du récupérateur de condensats ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état et nettoyage de la tête de combustion ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état et nettoyage de l&#146;électrode d&#146;ionisation  et des électrodes d&#146;allumage ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état et nettoyage des filtres FOD ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle étanchéité des raccords FOD  ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle connexions boite à bornes du moteur ventilateur ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Graissage des paliers du moteur et du ventilateur ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle du servomoteur, des volets et de la tringlerie du système modulant ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle de la dépression foyer ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle du tarage des soupapes de sécurité ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Ramonage du conduit de fumées, du carneau et de la chaudière (opération réalisée par un prestataire) ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état des réfractaires et de l'étanchéité des portes et trappes de visites ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle état du calorifuge ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Contrôle de la présence et de l'état du bac de rétention sous brûleur ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-FU","Brûleur fuel ","BRU6M-FU","Brûleur fuel "," ","[...] Mise à jour du livret de chaufferie",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU1A-GA","Brûleur gaz "," ","[...] Ramonage du conduit de fumées, du carneau et de la chaudière (opération réalisée par un prestataire) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU1A-GA","Brûleur gaz "," ","[...] Contrôle état des réfractaires et de l'étanchéité des portes et trappes de visites ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU1A-GA","Brûleur gaz "," ","[...] Contrôle état du calorifuge ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU1A-GA","Brûleur gaz "," ","[...] Mise à jour du livret de chaufferie",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","[...] Contrôle brûleur et analyse de la combustion (CO², CO,T°C fumées, indice de noircissement, rendement) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","[...] Mise à jour du livret de chaufferie ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","NOTA.: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","Chaudière neuve (mise en service après le 13/03/00)  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","  - rendement : 90% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","Chaudière existante ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","  - Entre 400 et 2000kW -> rendement 86% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","  - Entre 2000 et 10 000kW -> rendement 87% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU3M-GA","Brûleur gaz "," ","  - Entre 10 000 et 50 000kW -> rendement 88% ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle état et man&#156;uvre des vannes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle débit et des sondes de températures départ/retour ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle et essai des sécurités ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle état du récupérateur de condensats ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle état et nettoyage de la tête de combustion ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle état et nettoyage de l&#146;électrode d&#146;ionisation  et des électrodes d&#146;allumage ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle état et nettoyage des filtres gaz ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle étanchéité des raccords gaz à la pression de service  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle connexions boite à bornes du moteur ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle du servomoteur, des volets et de la tringlerie du système modulant ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle de la dépression foyer ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Contrôle du tarage des soupapes de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-GA","Brûleur gaz ","BRU6M-GA","Brûleur gaz "," ","[...] Mise à jour du livret de chaufferie",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle brûleur et analyse de la combustion (CO², CO,T°C fumées, indice de noircissement, rendement)  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","[...] Mise à jour du livret de chaufferie ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","NOTA.: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","Chaudière neuve (mise en service après le 13/03/00) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","  - Rendement : 89% ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","Chaudière existante ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","  - Entre 400 et 2000kW = 85% ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","  - Entre 2000 et 10 000kW = 86% ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU3M-MI","Brûleur mixte gaz/fuel "," ","  - Entre 10 000 et 50 000kW =87%  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état et man&#156;uvre des vannes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle débit et des sondes de températures départ/retour ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle et essai des sécurités ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état du récupérateur de condensats ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état et nettoyage de la tête de combustion ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état et nettoyage de la cellule détection flamme,de la sonde d'ionisation et des électrodes d'allumage ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état et nettoyage des filtres FOD ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle étanchéité des raccords gaz et FOD ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle connexions boite à bornes du moteur ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Graissage des paliers du moteur et du ventilateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle du servomoteur, des volets et de la tringlerie du système modulant ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle de la dépression foyer ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle du tarage des soupapes de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Ramonage du conduit de fumées, du carneau et de la chaudière (opération réalisée par un prestataire) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état des réfractaires et de l'étanchéité des portes et trappes de visites ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle état du calorifuge ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Contrôle de la présence et de l'état du bac de rétention sous brûleur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BRU-MI","Brûleur mixte gaz/fuel ","BRU6M-MI","Brûleur mixte gaz/fuel "," ","[...] Mise à jour du livret de chaufferie",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EA","Batterie terminale d'eau","BTE1A-EA","Batterie terminale d'eau"," ","[...] Nettoyage et désinfection du bac de récupération des condensats (si présence) ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EA","Batterie terminale d'eau","BTE1A-EA","Batterie terminale d'eau"," ","[...] Contrôle de l'étanchéité des batteries ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EA","Batterie terminale d'eau","BTE1A-EA","Batterie terminale d'eau"," ","[...] Relevé des pertes de charge du circuit eau batteries",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EL","Batterie Terminale électrique","BTE1A-EL","Batterie Terminale électrique"," ","[...] Contrôle de la régulation ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EL","Batterie Terminale électrique","BTE1A-EL","Batterie Terminale électrique"," ","[...] Vérification des intensités absorbées ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EL","Batterie Terminale électrique","BTE1A-EL","Batterie Terminale électrique"," ","[...] Vérification de l'état des épingles ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EL","Batterie Terminale électrique","BTE1A-EL","Batterie Terminale électrique"," ","[...] Contrôle des thermostats de sécurité ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","BTE-EL","Batterie Terminale électrique","BTE1A-EL","Batterie Terminale électrique"," ","[...] Resserrage des connexions",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAL","Caloduc","CAL1A","Caloduc"," ","[...] Nettoyage de la batterie ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAL","Caloduc","CAL1A","Caloduc"," ","[...] Contrôle de la charge en fluide frigorigène",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAL","Caloduc","CAL3M","Caloduc"," ","[...] Remplacement des filtres selon besoin",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle du fonctionnement des commutateurs Chaud/Froid/Ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle du fonctionnement du thermostat ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle du fonctionnement de la régulation ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle des connexions électriques ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle des protections électriques ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle et dépoussiérage de la batterie évaporateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Vérification de l'étanchéité des joints et des flexibles ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle de l'écoulement et pompe de relevage éventuelle ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Nettoyage du bac à condensât ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle du filtre et remplacement si nécessaire ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle et dépoussiérage du moto ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Nettoyage complet de l'unité intérieure ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle de la vanne pressostatique ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Vérification de l'étanchéité des joints et des flexibles ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Contrôle vanne d'isolement ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO1A","Console à eau"," ","[...] Relevé du compteur d'eau",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO6M","Console à eau"," ","[...] Contrôle de la disponibilité ",0.05,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAO","Console à eau","CAO6M","Console à eau"," ","[...] Contrôle du filtre et remplacement si nécessaire",0.05,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle du fonctionnement des commutateurs Chaud/Froid/Ventilateur ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle du fonctionnement du thermostat ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle du fonctionnement de la régulation ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle des connexions électriques ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle des protections électriques ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle et dépoussiérage de la batterie évaporateur ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Vérification de l'étanchéité des joints et des flexibles ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle de l'écoulement et pompe de relevage éventuelle ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Nettoyage du bac à condensât ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle du filtre et remplacement si nécessaire ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Contrôle et dépoussiérage du moto ventilateur ",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS1A","Cassette plafonnière"," ","[...] Nettoyage complet de l'unité intérieure",0.8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS6M","Cassette plafonnière"," ","[...] Contrôle de la disponibilité ",0.1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CAS","Cassette plafonnière","CAS6M","Cassette plafonnière"," ","[...] Contrôle du filtre et remplacement si nécessaire",0.1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF1A","Clapet coupe feu"," ","[...] Contrôle du contact de fin de course et du report service de sécurité ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF1A","Clapet coupe feu"," ","[...] Contrôle des asservissements ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF1A","Clapet coupe feu"," ","[...] Contrôle des joints de scellement et des matériaux réfractaires ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF1A","Clapet coupe feu"," ","[...] Vérification du fonctionnement de la commande manuelle ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF1A","Clapet coupe feu"," ","[...] Enregistrement des essais et contrôles dans le registre de sécurité et sur BT préventif",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CCF","Clapet coupe feu","CCF3M","Clapet coupe feu"," ","[...] Contrôle par simulation du bon fonctionnement des détecteurs et des fusibles",0.1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX1A","Caisson d'extraction d'air"," ","[...] Nettoyage intérieur complet du caisson, ventilateurs, registres... ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX1A","Caisson d'extraction d'air"," ","[...] Nettoyage intérieur complet du circuit de récupération de chaleur si existant ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX1A","Caisson d'extraction d'air"," ","[...] Mesure et enregistrement de la pression statique ou de la vitesse d'air aux points caractéristiques de l'installation",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle des raccordements sur la boite à bornes du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de l'état de la tension des courroies ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de l'alignement des poulies ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle des roulements et graissage des paliers ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de la fixation des volutes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Graissage des registres et contrôle des moto-réducteurs ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de l'état des soufflets et plots antivibratiles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","[...] Mesure et enregistrement du débit global minimal d'air extrait de l'installation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CEX","Caisson d'extraction d'air","CEX6M","Caisson d'extraction d'air"," ","NOTA.: Si contractuel, Entretien et ramonage des gaines d'extraction d'air vicié, de buée de graisse (Opération s/traitée) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle état et man&#156;uvre des vannes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle du débit et des sondes de températures départ/retour ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle et essai des sécurités ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Essai de soupapes de sécurité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle des connexions des résistances ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle de l'isolement des résistances ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-EL","Chaudière électrique ","CHA1A-EL","Chaudière électrique "," ","[...] Contrôle de l'intensité absorbée par les résistances",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-FU","Chaudière Fuel (Hors Brûleur)"]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-GA","Chaudière Gaz (Hors Brûleur)"]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle des points de consignes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle de la pression d'eau du réseau chauffage ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle état et man&#156;uvre des vannes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Nettoyage externe du corps de chauffe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle étanchéité des raccords gaz ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle de l'état du récupérateur de condensats   ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle état et nettoyage du thermo-couple      ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle état des électrodes d'allumage      ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Nettoyage de la veilleuse ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Contrôle des aérations hautes et basses ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Essai des sécurités ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MG","Chaudière murale Gaz","CHA1A-MG","Chaudière murale Gaz"," ","[...] Ramonage du conduit de fumée ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-MI","Chaudière Mixte (Hors Brûleur)"]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Analyse physico chimique par un laboratoire spécialisé (PH, TH, TCL, SiO2, Na2S03,Fe, Cu, salinité) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Contrôle brûleur et analyse de la combustion (CO², CO, T°C fumées ,indice de noircissement, rendement) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Contrôle état et man&#156;uvre des vannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Contrôle de la régulation de remplissage ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Essai des sécurités et du dispositif de détection gaz ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Contrôle état et nettoyage de la tête de combustion ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA3M-VA","Chaudière vapeur"," ","[...] Contrôle état et nettoyage de l&#146;électrode d&#146;ionisation ou cellule détection flamme et des électrodes d&#146;allumage",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle état et nettoyage des filtres ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle étanchéité des raccords gaz à l'aide d'un produit moussant et FOD à la pression de service  ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle connexions boite à bornes du moteur ventilateur ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Graissage des paliers du moteur et du ventilateur ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle du servomoteur, des volets et de la tringlerie du système modulant ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle de la dépression foyer ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Essai des soupapes de sécurité (opération réalisée par un prestataire) ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Dépose des tampons autoclaves d'accès aux trous d'hommes ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Dépose de la trappe d'accès à la chambre de combustion, le cas échéant dépose du brûleur ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Dépose des panneaux boulonnés le long du faisceau de convection ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Nettoyage sous pression des parois rendus accessibles ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Remontage et remplacement des joints ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle état des réfractaires et de l'étanchéité des portes et trappes de visites ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Contrôle état du calorifuge ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CHA-VA","Chaudière vapeur","CHA6M-VA","Chaudière vapeur"," ","[...] Ramonage du conduit de fumées, du carneau de la chaudière (opération réalisée par un prestataire)",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Contrôle de l'intensité absorbée et de l'isolement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Relevé du delta P de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Contrôle des roulements ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CIR","Circulateur","CIR6M","Circulateur"," ","[...] Contrôle de la fixation et des supports antivibratiles",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CLA","Clarificateur"]
["CVCD","Chauf - Ventil - Clim - Desenf","COR","Cordon chauffant","COR1A","Cordon chauffant"," ","[...] Contrôle de la consigne ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","COR","Cordon chauffant","COR1A","Cordon chauffant"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","COR","Cordon chauffant","COR1A","Cordon chauffant"," ","[...] Contrôle des connexions électriques ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","COR","Cordon chauffant","COR1A","Cordon chauffant"," ","[...] Contrôler la qualité diélectrique du cordon à 500 V (supérieur à 10 Mégohms entre T et conducteurs)   ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","COR","Cordon chauffant","COR1A","Cordon chauffant"," ","[...] Contrôler l'intensité et la tension sur le départ du tableau basse tension",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","Régulation: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Dépoussiérage des cartes ou des régulateurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Contrôle serrage des connexions ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Vérification des points de consignes ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Vérification des valeurs de gain en proportionnel, intégral et dérivé ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Contrôle de l'état de fonctionnement des actionneurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Contrôle de l'état et de la cohérence des indications des capteurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Contrôle des lois de régulations ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," "," ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","Mesures: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Mesure et enregistrement des performances ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Mesure et enregistrement de la pression statique ou de la vitesse d'air aux points caractéristiques de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Mesure et enregistrement du débit global minimal d'air neuf de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA1A-EA R","CTA batterie à eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","Compartiment filtration: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","[...] Remplacement des filtres si la perte de charge est supérieure à la recommandation du constructeur  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","[...] Relevé de la perte de charge avant et après le remplacement des filtres ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","[...] Contrôle de l'étanchéité  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","Mesures: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA3M-EA","CTA batterie à eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Caisson: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Nettoyage extérieur complet du caisson ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Nettoyage intérieur complet du caisson, ventilateurs, batteries, registres... ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de l'état des soufflets et plots antivibratiles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle presses étoupes vannes et servomoteur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Compartiment moteur: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle des raccordements sur la boite à bornes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de l'état de la tension des courroies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de l'alignement des poulies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle des roulements et graissage des paliers ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de la fixation des volutes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de la cohérence des appareils de mesure ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Compartiment batterie chaude et froide: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle du bon écoulement des eaux de récupération des condensats batterie eau froide ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Nettoyage et désinfection du bac de récupération des condensats  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Essais du thermostat antigel et contrôle des asservissements ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Contrôle de l'étanchéité des batteries ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Graissage des registres et contrôle des moto-réducteurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Relevé des pertes de charge du circuit eau batteries ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Nota.: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Les équipements doivent être nettoyés et désinfectés avec une solution de chlore concentré à 50 milligrammes de chlore libre par litre d'eau froide ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EA","CTA d'air avec batterie à eau","CTA6M-EA","CTA batterie à eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","Régulation: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Dépoussiérage des cartes ou des régulateurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Contrôle serrage des connexions ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Vérification des points de consignes ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Vérification des valeurs de gain en proportionnel, intégral et dérivé ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Contrôle de l'état de fonctionnement des actionneurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Contrôle de l'état et de la cohérence des indications des capteurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Contrôle des lois de régulations ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," "," ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","Mesures: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Mesure et enregistrement des performances ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Mesure et enregistrement de la pression statique ou de la vitesse d'air aux points caractéristiques de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Mesure et enregistrement du débit global minimal d'air neuf de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA1A-EE R","CTA batterie électrique & eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","Compartiment filtration: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","[...] Remplacement des filtres si la perte de charge est supérieure à la recommandation du constructeur  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","[...] Relevé de la perte de charge avant et après le remplacement des filtres ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'étanchéité  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","Mesures: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA3M-EE","CTA batterie électrique & eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Caisson: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Nettoyage extérieur complet du caisson ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Nettoyage intérieur complet du caisson, ventilateurs, batteries, registres... ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'état des soufflets et plots antivibratiles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle presses étoupes vannes et servomoteur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Compartiment moteur: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle des raccordements sur la boite à bornes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'état de la tension des courroies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'alignement des poulies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle des roulements et graissage des paliers ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de la fixation des volutes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de la cohérence des appareils de mesure ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Compartiment batterie électrique: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'intensité et de l'isolement des différents étages de la batterie électrique ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Essai des sécurités de la batterie électrique ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Compartiment batterie chaude et froide: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle du bon écoulement des eaux de récupération des condensats batterie eau froide ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Nettoyage et désinfection du bac de récupération des condensats  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Essais du thermostat antigel et contrôle des asservissements ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Contrôle de l'étanchéité des batteries ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Graissage des registres et contrôle des moto-réducteurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Relevé des pertes de charge du circuit eau batteries ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Nota.: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Les équipements doivent être nettoyés et désinfectés avec une solution de chlore concentré à 50 milligrammes de chlore libre par litre d'eau froide ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EE","CTA avec batterie élec & eau","CTA6M-EE","CTA batterie électrique & eau"," ","[...] Consignation des interventions dans le livret d'entretien CTA",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","Régulation: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Dépoussiérage des cartes ou des régulateurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Contrôle serrage des connexions ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Vérification des points de consignes ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Vérification des valeurs de gain en proportionnel, intégral et dérivé ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Contrôle de l'état de fonctionnement des actionneurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Contrôle de l'état et de la cohérence des indications des capteurs ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Contrôle des lois de régulations ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," "," ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","Mesures: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Mesure et enregistrement des performances ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Mesure et enregistrement de la pression statique ou de la vitesse d'air aux points caractéristiques de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Mesure et enregistrement du débit global minimal d'air neuf de l'installation ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA1A-EL","CTA Batterie électrique"," ","[...] Consignation des interventions dans le livret d'entretien CTA",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","Compartiment filtration: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","[...] Remplacement des filtres si la perte de charge est supérieure à la recommandation du constructeur  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","[...] Relevé de la perte de charge avant et après le remplacement des filtres ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'étanchéité  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","[...] Consignation des interventions dans le livret d'entretien CTA ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","Mesures: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA3M-EL","CTA Batterie électrique"," ","[...] Consignation des interventions dans le livret d'entretien CTA",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Caisson: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Nettoyage extérieur complet du caisson ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Nettoyage intérieur complet du caisson, ventilateurs, batteries, registres... ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'état des soufflets et plots antivibratiles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle presses étoupes vannes et servomoteur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Compartiment moteur: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle des raccordements sur la boite à bornes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'état de la tension des courroies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'alignement des poulies ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle des roulements et graissage des paliers ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de la fixation des volutes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de la cohérence des appareils de mesure ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Compartiment batterie électrique: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Contrôle de l'intensité et de l'isolement des différents étages de la batterie électrique ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Essai des sécurités de la batterie électrique ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Nota.: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Les équipements doivent être nettoyés et désinfectés avec une solution de chlore concentré à 50 milligrammes de chlore libre par litre d'eau froide ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CTA-EL","CTA avec Batterie électrique","CTA6M-EL","CTA Batterie électrique"," ","[...] Consignation des interventions dans le livret d'entretien CTA",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Contrôle des fixations ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Contrôle de l'isolement ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Contrôle du thermostat et de la régulation  ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Vérification des raccordements et de l'état des câbles ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Dépoussiérage et nettoyage  ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Contrôle de la programmation horaire ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","CVE","Convecteur électrique","CVE1A","Convecteur électrique"," ","[...] Contrôle de la liaison à la terre",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES3M","Ventilateur de désenfumage"," ","[...] Essai du ventilateur, du coffret de relayage ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES3M","Ventilateur de désenfumage"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES3M","Ventilateur de désenfumage"," ","NOTA.: Dans les IGH, l'essai trimestriel doit être effectué par le service de sécurité",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'état général ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de la turbine et du jeu d'arbre ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'état de la protection mécanique des courroies ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'état de la tension des courroies ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'alignement des poulies ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle des roulements et graissage des paliers ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle des raccordements sur la boite à borne moteur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'intensité et de l'isolement du moteur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'état de la cage ou des grilles ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de la fixation du ventilateur et du moteur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Contrôle de l'état des plots antivibratiles ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DES","Ventilateur de désenfumage","DES6M","Ventilateur de désenfumage"," ","[...] Nettoyage complet",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle des ventilateurs (fixation, graissage) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de l'état des hélices ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Nettoyage et peignage des batteries ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle et examen des ailettes des batteries ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de l'état des manchons et plots anti-vibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle du supportage et de la carrosserie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de l'état de la carrosserie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de l'état des canalisations ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de l'isolement et de l'intensité absorbée des moteurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Resserrage des connexions électriques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Contrôle de la régulation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY","Dry cooler","DRY1A","DryCooler"," ","[...] Mesure des performances (Lors de l'identification d'un dysfonctionnement.)",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle de l'état des canalisations ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Mesure des performances (Lors de l'identification d'un dysfonctionnement.)  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Nettoyage et désinfection de l&#146;installation (annuel) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","Entretien des rampes de pulvérisation: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Assurer le démontage des têtes de pulvérisations puis leur nettoyage ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","Entretien des corps d&#146;échange (échangeur): ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Nettoyage et peignage des batteries ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle et examen des ailettes des batteries ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","Entretien des ventilateurs: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle des ventilateurs (fixation, graissage) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle de l'état des hélices ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle de l'état des manchons et plots anti-vibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle du supportage et de la carrosserie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Resserrage des connexions électriques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle de l'isolement et de l'intensité absorbée des moteurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1A-PU","DryCooler adiabatique pulv eau"," ","[...] Contrôle de la régulation",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","Entretien des rampes de pulvérisation: ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","[...] Vérification du bon écoulement des têtes de pulvérisations ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","[...] Vérification du bon fonctionnement de l'électrovanne. ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," "," ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","Entretien des corps d&#146;échange (échangeur): ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","[...] Surveillance visuelle des parties basses et hautes du corps d&#146;échange. ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","DRY-PU","Dry cooler adiab à pulvé d'eau","DRY1M-PU","DryCooler adiabatique pulv eau"," ","[...] Selon l&#146;état d&#146;encrassement, un démontage puis un nettoyage mécanique sont à entreprendre.",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH1A-PL","Echangeur à plaques"," ","[...] Nettoyage du filtre ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH1A-PL","Echangeur à plaques"," ","[...] Détartrage mécanique ou chimique si nécessaire",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH6M-PL","Echangeur à plaques"," ","[...] Contrôle des presses étoupe des vannes ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH6M-PL","Echangeur à plaques"," ","[...] Man&#156;uvres des vannes d'isolement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH6M-PL","Echangeur à plaques"," ","[...] Contrôle du calorifuge ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH6M-PL","Echangeur à plaques"," ","[...] Contrôle de la perte de charge primaire ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-PL","Echangeur à plaques","ECH6M-PL","Echangeur à plaques"," ","[...] Contrôle de la perte de charge secondaire",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH1A-TU","Echangeur tubulaire"," ","[...] Nettoyage du filtre ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH1A-TU","Echangeur tubulaire"," ","[...] Détartrage mécanique ou chimique si nécessaire",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH6M-TU","Echangeur tubulaire"," ","[...] Contrôle des presses étoupe des vannes ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH6M-TU","Echangeur tubulaire"," ","[...] Man&#156;uvres des vannes d'isolement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH6M-TU","Echangeur tubulaire"," ","[...] Contrôle du calorifuge ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH6M-TU","Echangeur tubulaire"," ","[...] Contrôle de la perte de charge primaire ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ECH-TU","Echangeur tubulaire","ECH6M-TU","Echangeur tubulaire"," ","[...] Contrôle de la perte de charge secondaire",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EJE","Ejecto-convecteur"]
["CVCD","Chauf - Ventil - Clim - Desenf","EXP","Vase et réservoir d'expansion","EXP1A","Vase et réservoir d'expansion"," ","[...] Contrôle de la pression de gonflage  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXP","Vase et réservoir d'expansion","EXP1A","Vase et réservoir d'expansion"," ","[...] Contrôle de la date d'épreuve de l'appareil sous pression  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXP","Vase et réservoir d'expansion","EXP1A","Vase et réservoir d'expansion"," ","[...] Date de la dernière épreuve:&#133;&#133;&#133;&#133;&#133;&#133;&#133;&#133;",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Contrôle de l'alimentation électrique ou pneumatique ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Vérification fonctionnelle de la commande manuelle ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Contrôle de l'état de la sparklet ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Contrôle des joints de scellement et des matériaux réfractaires ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Contrôle mécanique des pièces en mouvement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","EXU","Exutoire de fumée","EXU6M","Exutoire de fumée"," ","[...] Essai des exutoires",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","FILT UI","Filtres des unités intérieure"]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR1A-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle de l'étanchéité des circuits frigorifiques >2 Kg ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR1A-CE","Groupe frigorifique centrifuge"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR1A-CE","Groupe frigorifique centrifuge"," ","NOTA: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR1A-CE","Groupe frigorifique centrifuge"," ","Attention remplir le certificat de recherche de fuite annuelle",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","Opération réalisée par un prestataire: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle du fonctionnement général ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Transfert du fluide frigorifique ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Déshydratation des circuits réfrigérants ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Remplacement des cartouches de filtration des circuits réfrigérants ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle de la bonne rotation des aubes ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Vidange de l'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Nettoyage du carter d'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Remplacement des filtres d'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle de la pompe à huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Remplissage huile neuve ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Vérification du niveau d'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle du thermostat température d'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Nettoyage de la chambre de purge ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle du clapet à flotteur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle du pressostat de commande ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des clapets de la pompe de purge ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Essai des pressostats HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Essai du thermostat antigel ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des intensités absorbées ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle de l'étanchéité des circuits frigorifiques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des connexions électriques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle de l'isolement des moteurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des pertes de charges du condenseur et de l'évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des plots antivibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-CE","Groupe frigorifique centrifuge","GFR6M-CE","Groupe frigorifique centrifuge"," ","[...] Contrôle des manchons de dilatation",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR1A-PI","Groupe frigorifique à piston"," ","[...] Contrôle de l'étanchéité des circuits frigorifiques >2 Kg ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR1A-PI","Groupe frigorifique à piston"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR1A-PI","Groupe frigorifique à piston"," ","NOTA: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR1A-PI","Groupe frigorifique à piston"," ","Attention remplir le certificat de recherche de fuite annuelle",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle du fonctionnement général ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle de la charge en fluide frigorigène ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle des pertes de charges du condenseur et de l'évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Essai des pressostats HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Essai de la sonde de présence d'eau évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Essai du thermostat antigel ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle des intensités absorbées ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle de l&#146;état de la ou des batterie(s) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle de l&#146;état du ou des ventilateur(s) ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle des connexions électriques des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle de l'isolement des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Changement du déshydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Test de l'acidité de l'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle des plots anti-vibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle des manchons de dilatation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Vidange en fonction des nombres d'heures de fonctionnement ou de résultat négatif des tests d'acidité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Contrôle de l'état de calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-PI","Groupe frigorifique à piston","GFR6M-PI","Groupe frigorifique à piston"," ","[...] Mesure des performances",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR1A-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de l'étanchéité des circuits frigorifiques >2 Kg ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR1A-SC","Groupe frigorifique typ Scroll"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR1A-SC","Groupe frigorifique typ Scroll"," ","NOTA: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR1A-SC","Groupe frigorifique typ Scroll"," ","Attention remplir le certificat de recherche de fuite annuelle",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","Opération réalisée par un prestataire: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle du fonctionnement général ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de la charge en fluide frigorigène ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle des pertes de charge du condenseur et de l&#146;évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle surchauffe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Essai des pressostats HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Essai de la sonde de présence d&#146;eau évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Essai du thermostat antigel et du pressostat huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle des intensités absorbées ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de l&#146;étanchéité des circuits frigorifiques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de l&#146;état du ventilateur et de la batterie ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle des connexions électriques des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de l&#146;isolement des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Changement du déshydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Test de l&#146;acidité de l&#146;huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle des plots antivibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle des manchons de dilatation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Vidange en fonction des nombres d&#146;heures de fonctionnement ou du résultat négatif des tests d&#146;acidité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Nettoyage ventilateur et ailettes de la batterie  ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Désembouage évaporateur si besoin ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Contrôle de l&#146;état des calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-SC","Groupe frigorifique Scroll","GFR6M-SC","Groupe frigorifique typ Scroll"," ","[...] Mesure des performances",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR1A-VI","Groupe frigorifique à vis"," ","[...] Contrôle de l'étanchéité des circuits frigorifiques >2 Kg ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR1A-VI","Groupe frigorifique à vis"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR1A-VI","Groupe frigorifique à vis"," ","NOTA: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR1A-VI","Groupe frigorifique à vis"," ","Attention remplir le certificat de recherche de fuite annuelle",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","Opération réalisée par un prestataire: ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," "," ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle du fonctionnement général ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle des pertes de charge du condenseur et de l&#146;évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle surchauffe ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Essai des pressostats HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Essai de la sonde de présence d&#146;eau évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Essai du thermostat antigel et du pressostat huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle des intensités absorbées ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle de l&#146;étanchéité des circuits frigorifiques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle des connexions électriques des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle de l&#146;isolement des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Changement du déshydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Test de l&#146;acidité de l&#146;huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle des plots antivibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle des manchons de dilatation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Vidange en fonction des nombres d&#146;heures de fonctionnement ou du résultat négatif des tests d&#146;acidité ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Détartrage du condenseur si besoin ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Désembouage évaporateur si besoin ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Contrôle de l&#146;état des calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","GFR-VI","Groupe frigorifique à vis","GFR6M-VI","Groupe frigorifique à vis"," ","[...] Mesure des performances",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-AT","Humidificateur Atomiseur","HUM3M-AT","Humidificateur Atomiseur"," ","[...] Vidange, nettoyage et contrôle de l'étanchéité du bac ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-AT","Humidificateur Atomiseur","HUM3M-AT","Humidificateur Atomiseur"," ","[...] Contrôle de l'étanchéité des raccordements pneumatiques ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-AT","Humidificateur Atomiseur","HUM3M-AT","Humidificateur Atomiseur"," ","[...] Contrôle et nettoyage des buses d'injection ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-AT","Humidificateur Atomiseur","HUM3M-AT","Humidificateur Atomiseur"," ","[...] Contrôle flotteur et électrovanne d'alimentation automatique en eau",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle du taux de déconcentration ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle de la pompe de recyclage ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle et man&#156;uvre du système de vidange automatique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle flotteur et électrovanne d'alimentation automatique en eau ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle et nettoyage des buses de pulvérisation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle de l'étanchéité du bac ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Nettoyage et désinfection du bac par solution chlorée ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Contrôle de l'état des nids d'abeilles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","[...] Dépose des nids d&#146;abeilles en cas d'arrêt ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","NOTA.: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-LA","Humidificateur Laveur","HUM3M-LA","Humidificateur Laveur ruislmnt"," ","Les équipements doivent être nettoyés et désinfectés avec une solution de chlore concentré à 50 milligrammes de chlore libre par litre d'eau froide",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Vidange des humidificateurs en période de non humidification ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Contrôle de l'intensité nominale et de l'isolement des électrodes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Contrôle et nettoyage des buses d'injection ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Contrôle flotteur et électrovanne d'alimentation automatique en eau ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Contrôle et man&#156;uvre du système de vidange automatique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Contrôle de l'étanchéité des raccordements vapeur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","HUM-VA","Humidificateur vapeur","HUM3M-VA","Humidificateur vapeur"," ","[...] Nettoyage de la cuve et des électrodes",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MOD","Moduline","MOD1A","Moduline"," ","[...] Contrôle de la régulation, du bilame ",0.15,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MOD","Moduline","MOD1A","Moduline"," ","[...] Nettoyage",0.15,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle du pressostat de commande ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle des pressions d'asservissement et des report d'alarme ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de l'intensité moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de l'isolement et des liaisons équipotentielles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle des roulements et graissage éventuel ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de l'accouplement ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de la protection mécanique des parties tournantes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle de la fixation de l'ensemble et des plots antivibratiles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle du filtre à tamis et nettoyage éventuel ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle du fonctionnement du clapet anti-retour ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Contrôle des déverseurs ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Vidange et rinçage de la bâche ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MPR","Maintien de pression","MPR6M","Maintien de pression"," ","[...] Remplacement de la signalisation si nécessaire",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle de l'état des raccordements hydrauliques et des calorifuges ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle de l'état et nettoyage du conduit d'évacuation des condensats ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle de l'état de la connectique de la platine de régulation et de commande ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle de l'état des câbles d'alimentation électrique ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle du filtre et remplacement si nécessaire ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle du fonctionnement du moto-ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle du fonctionnement de la régulation et des vannes motorisées ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Contrôle et enregistrement de tous les paramètres de fonctionnement ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Essai des commandes groupées et des reports d'information GTB ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA1A","Module de traitement d'air"," ","[...] Essai des disjoncteurs différentiels",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA6M","Module de traitement d'air"," ","[...] Contrôle de la disponibilité ",0.05,5]
["CVCD","Chauf - Ventil - Clim - Desenf","MTA","Module de traitement d'air","MTA6M","Module de traitement d'air"," ","[...] Contrôle du filtre et remplacement si nécessaire",0.05,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC1A","Pompe à chaleur"," ","[...] Contrôle étanchéité éléments constituant le confinement des fluides frigorigènes >2 Kg ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC1A","Pompe à chaleur"," "," ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC1A","Pompe à chaleur"," ","Nota.: ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC1A","Pompe à chaleur"," ","Attention remplir le certificat de recherche de fuite annuelle",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de la régulation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle des pressostats HP/BP ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de la sonde d'eau condenseur/évaporateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle du thermostat antigel ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle du réglage du détendeur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de l'intensité des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de l'isolement des compresseurs ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Remplacement du déshydrateur ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de l'acidité de l'huile ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle des plots antivibratiles ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle des manchons de dilatation ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle de l'état des calorifuges ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Contrôle des connexions électriques ",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC","Pompe à chaleur","PAC6M","Pompe à chaleur"," ","[...] Mesure des performances",4,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle du fonctionnement du thermostat  ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de la commande Chaud/Froid/Vitesse ventilateur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle des connexions électriques et état des câbles ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'état de la batterie évaporateur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'écoulement et pompe de relevage éventuelle ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Nettoyage du bac à condensât ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle du fonctionnement du ventilateur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'intensité et tension du ventilateur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de la charge frigorifique et de l'étanchéité du circuit ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'acidité du fluide frigorigène ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle du filtre deshydrateur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle des pressions HP/BP ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle des pressostats HP/BP (Chaîne de sécurité) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'intensité et l'isolement du compresseur ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de la tension du compresseur en fonctionnement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle de l'état du calorifuge ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle des presse étoupes ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC1A-BO","Pompe à chaleur sur boucle"," ","[...] Nettoyage complet de l'unité intérieure",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PAC-BO","Pompe à chaleur sur boucle","PAC6M-BO","Pompe à chaleur sur boucle"," ","[...] Contrôle du filtre et remplacement si nécessaire",0.1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","ECHANGEUR ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Vérification des performance (notamment l&#146;écart de température entre la sortie des condensats et le retour du secondaire) et le nettoyage  si nécessaire ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Contrôle des organes de sécurité(thermostats, pressostats, soupapes) ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Vérification des joints et de la boulonnerie ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," "," ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","REGULATION ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Vérification des capteurs  ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Vérification des actionneurs ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," "," ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","CIRCUIT VAPEUR ET CONDENSATS ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Contrôle de l&#146;état extérieur des tuyauteries ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Contrôle général du fonctionnement ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Man&#156;uvre des robinets ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Graissage des tiges de robinets ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Graissage des tiges de servomoteur des vannes de régulation ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Nettoyage des clapet anti-retour ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Nettoyage du séparateur ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-ES","Prod Chauf Urb Eau Surchauffée","PCU1A-ES","Prod Chauf Urbain Eau Surchauf"," ","[...] Nettoyage de la bâche des condensats et réfection des protections anti-rouille si nécessaire",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PCU-VA","Prod Chauffage Urbain Vapeur"]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle du fonctionnement des commutateurs Chaud/Froid ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle du bon fonctionnement de la régulation et des électrovannes ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle des connexions électriques ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle calorifuge et état extérieur ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle du fonctionnement normal de la batterie électrique ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle du thermostat de sécurité ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR1A","Poutre froide"," ","[...] Contrôle de l' encombrement ",0.2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PFR","Poutre froide","PFR6M","Poutre froide"," ","[...] Contrôle de la disponibilité",0.1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle de l'état de l'accouplement et de sa protection mécanique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle de l'intensité absorbée et de l'isolement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Relevé du delta P de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle des roulements ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle de l'alignement du moteur et de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-AA","Pompe Double avec accouplement","PPD6M-AA","Pompe Double avec accouplement"," ","[...] Contrôle de la fixation et des supports antivibratiles",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle de l'état de l'accouplement et de sa protection mécanique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle de l'intensité absorbée et de l'isolement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Relevé du delta P de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle des roulements ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle de l'alignement du moteur et de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPD-SA","Pompe Double sans accouplement","PPD6M-SA","Pompe Double sans accouplement"," ","[...] Contrôle de la fixation et des supports antivibratiles",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle de l'état de l'accouplement et de sa protection mécanique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle de l'intensité absorbée et de l'isolement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Relevé du delta P de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle des roulements ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle de l'alignement du moteur et de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-AA","Pompe Simple avec accouplement","PPS6M-AA","Pompe Simple avec accouplement"," ","[...] Contrôle de la fixation et des supports antivibratiles",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle de l'état de l'accouplement et de sa protection mécanique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle de l'intensité absorbée et de l'isolement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Relevé du delta P de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle des roulements ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle de l'alignement du moteur et de la pompe ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PPS-SA","Pompe Simple sans accouplement","PPS6M-SA","Pompe Simple sans accouplement"," ","[...] Contrôle de la fixation et des supports antivibratiles",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-EL","Panneau rayonnant électrique","PRA6M-EL","Panneau rayonnant électrique"," ","[...] Contrôle de l'intensité et de l'isolement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-EL","Panneau rayonnant électrique","PRA6M-EL","Panneau rayonnant électrique"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-EL","Panneau rayonnant électrique","PRA6M-EL","Panneau rayonnant électrique"," ","[...] Contrôle des connexions électriques ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-EL","Panneau rayonnant électrique","PRA6M-EL","Panneau rayonnant électrique"," ","[...] Dépoussiérage et nettoyage du déflecteur",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-GA","Panneau rayonnant gaz","PRA6M-GA","Panneau rayonnant gaz"," ","A faire",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","PRA-SO","Panneau solaire"]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle du bon fonctionnement de la régulation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle du filtre et remplacement si nécessaire ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Dépoussiérage des batteries et du moto ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle de l'intensité et de l'isolement du moto ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","Batterie chaude: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Purge de l'air de la batterie ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle du fonctionnement de la régulation et des électrovannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle de la robinetterie d'isolement, man&#156;uvre des vannes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle des presses étoupes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","Batterie électrique: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle de l'intensité batterie électrique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle des connexions électriques ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAC","Rideau d'air chaud","RAC6M","Rideau d'air chaud"," ","[...] Contrôle de l'état du calorifuge",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAD","Radiateur à eau","RAD1A","Radiateur à eau"," ","[...] Purge de l'air ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAD","Radiateur à eau","RAD1A","Radiateur à eau"," ","[...] Contrôle du robinet thermostatique ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAD","Radiateur à eau","RAD1A","Radiateur à eau"," ","[...] Contrôle de la robinetterie d'isolement ",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","RAD","Radiateur à eau","RAD1A","Radiateur à eau"," ","[...] Dépoussiérage",0.25,5]
["CVCD","Chauf - Ventil - Clim - Desenf","REA","Réseau aéraulique","REA1A","Réseau aéraulique"," ","[...] Vérification des gaines: étanchéité, raccordement ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","REA","Réseau aéraulique","REA1A","Réseau aéraulique"," ","[...] Nettoyage des grilles d'air neuf et de rejet ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","REA","Réseau aéraulique","REA1A","Réseau aéraulique"," ","[...] Contrôle des positions des registres ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","REA","Réseau aéraulique","REA1A","Réseau aéraulique"," ","[...] Nettoyage et réglage des bouches d'extraction VMC ",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","REA","Réseau aéraulique","REA1A","Réseau aéraulique"," ","[...] Nettoyage des diffuseurs de soufflage et d'extraction (Hors moduline)",8,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","Régulation: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Dépoussiérage des cartes ou des régulateurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle serrage des connexions ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Vérification des points de consignes ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Vérification des valeurs de gain en proportionnel, intégral et dérivé ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l'état de fonctionnement des actionneurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l'état et de la cohérence des indications des capteurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des lois de régulations ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle du fonctionnement général ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de la charge en fluide frigorigène ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des pertes de charge du condenseur et de l’évaporateur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle surchauffe ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Essai des pressostats HP/BP ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Essai de la sonde de présence d’eau évaporateur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Essai du thermostat antigel et du pressostat huile ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des intensités absorbées ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l’étanchéité des circuits frigorifiques ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l’état du ventilateur et de la batterie ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des connexions électriques des compresseurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l’isolement des compresseurs ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Changement du déshydrateur ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Test de l’acidité de l’huile ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des plots antivibratiles ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle des manchons de dilatation ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Vidange en fonction des nombres d’heures de fonctionnement ou du résultat négatif des tests d’acidité ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Nettoyage ventilateur et ailettes de la batterie  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Désembouage évaporateur si besoin ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Contrôle de l’état des calorifuges ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Mesure des performances ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Mesure et enregistrement des performances ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Mesure et enregistrement de la pression statique ou de la vitesse d'air aux points caractéristiques de l'installation ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO1A","ROOF TOP"," ","[...] Mesure et enregistrement du débit global minimal d'air neuf de l'installation",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","Compartiment filtration: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","[...] Remplacement des filtres si la perte de charge est supérieure à la recommandation du constructeur  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","[...] Relevé de la perte de charge avant et après le remplacement des filtres ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","[...] Contrôle de l'étanchéité  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","[...] Consignation des interventions dans le livret d'entretien CTA ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO3M","ROOF TOP"," ","[...] Consignation des interventions dans le livret d'entretien CTA",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","Compartiment filtration: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","[...] Remplacement des filtres si la perte de charge est supérieure à la recommandation du constructeur  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","[...] Relevé de la perte de charge avant et après le remplacement des filtres ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","[...] Contrôle de l'étanchéité  ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","[...] Consignation des interventions dans le livret d'entretien CTA ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," "," ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","Mesures: ",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","ROO","Roof-Top","ROO6M","Roof-Top"," ","[...] Consignation des interventions dans le livret d'entretien CTA",5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de l'état général ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle du fonctionnement du thermostat  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de la commande Chaud/Froid/Vitesse ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle des connexions électriques ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de l'état des câbles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","Split unité extérieure: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de la charge frigorifique et de l'étanchéité du circuit ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de l'acidité du fluide frigorigène ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle du filtre deshydrateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle des pressions HP/BP ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle des pressostats HP/BP (Chaîne de sécurité) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de l'intensité et l'isolement du compresseur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de la tension du compresseur en fonctionnement ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de l'état du calorifuge ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle du pressostat se sécurité haute pression ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle des silentblocs ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Nettoyage complet de l'unité extérieure ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-EX","Unité Ext Clim Split system","SPL6M-EX","Unité ext Climati Split system"," ","[...] Contrôle de la charge frigorifique et  de l'étanchéité du circuit",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'état général ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du fonctionnement de la régulation et des sécurités ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du fonctionnement du thermostat  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la commande Chaud/Froid/Vitesse ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle des connexions électriques ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'état des câbles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","Split unité intérieure: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la batterie évaporateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'écoulement et pompe de relevage éventuelle ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Nettoyage du bac à condensât ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du filtre et remplacement si nécessaire ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Nettoyage et dépoussiérage du ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'intensité du ventilateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la tension du ventilateur en fonctionnement ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du fonctionnement normal de la batterie électrique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du thermostat de sécurité ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Nettoyage complet de l'unité intérieure ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","Split unité extérieure: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la charge frigorifique et de l'étanchéité du circuit ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'acidité du fluide frigorigène ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du filtre deshydrateur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle des pressions HP/BP ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle des pressostats HP/BP (Chaîne de sécurité) ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'intensité et l'isolement du compresseur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la tension du compresseur en fonctionnement ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de l'état du calorifuge ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle du pressostat se sécurité haute pression ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle des silentblocs ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Nettoyage complet de l'unité extérieure ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SPL-MO","Climatiseur Mono Split system","SPL6M-MO","Climatiseur Mono Split system"," ","[...] Contrôle de la charge frigorifique et  de l'étanchéité du circuit",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","SST-PF","Ss Station Plafonds Rayonants"]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1A-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Vidange, nettoyage et désinfection des circuits d'eau et des parties périphériques. ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1A-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Renseignement du livret d'entretien  ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1A-FE","Tour Aéro-Réfrigérante fermée"," "," ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1A-FE","Tour Aéro-Réfrigérante fermée"," ","NOTA.: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1A-FE","Tour Aéro-Réfrigérante fermée"," ","Désinfection ( annuelle ou avant chaque remise en service après un arrêt prolongé) par choc chloré (30 à 50 mg/litre de chlore libre avec au moins 2 à 3 heures de circulation) puis rinçage. ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du bon fonctionnement du traitement d'eau ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Relevé du compteur d'eau d'appoint ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du niveau bas du bac ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Relevé des températures d'eau E/S ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du taux de déconcentration ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'état de propreté des surfaces ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Analyse d'eau pour recherche de LEGIONELLA (Opération réalisée par un prestataire) ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Renseignement du livret d'entretien  ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," "," ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","NOTA.: ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","Pour les installations soumises à autorisation recherche de légionelle mensuelle ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR1M-FE","Tour Aéro-Réfrigérante fermée"," ","Pour les installations soumises à déclaration recherche de légionelle bimestrille",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'état des packings et du circuit de pulvérisation ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'entartrage et de la corrosion du bac ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du système d'appoint d'eau ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du bon fonctionnement de la déconcentration automatique ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'intensité de la résistance antigel et du cordon chauffant ( voir gamme cordon chauffant ) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du delta P pompe de pulvérisation (tour à circuit fermé) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle du delta P batterie d'échange (tour à circuit fermé) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'état de la tension des courroies ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'état de la protection mécanique du système de transmission ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'alignement des poulies ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle roulements et graissage paliers ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle des raccordements sur la boite à bornes du moteur ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de la fixation des volutes ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de l'état des plots antivibratiles ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Contrôle de la cohérence des appareils de mesure ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Mesure et enregistrement des performances si nécessaire ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-FE","Tour Aéro-Réfrigérante fermée","TAR6M-FE","Tour Aéro-Réfrigérante fermée"," ","[...] Renseignement du livret d'entretien ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1A-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Vidange, nettoyage et désinfection des circuits d'eau et des parties périphériques. ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1A-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Renseignement du livret d'entretien  ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1A-OU","Tour Aéro-Réfrigérante ouverte"," "," ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1A-OU","Tour Aéro-Réfrigérante ouverte"," ","NOTA.: ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1A-OU","Tour Aéro-Réfrigérante ouverte"," ","Désinfection ( annuelle ou avant chaque remise en service après un arrêt prolongé) par choc chloré (30 à 50 mg/litre de chlore libre avec au moins 2 à 3 heures de circulation) puis rinçage. ",6,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du bon fonctionnement du traitement d'eau ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Relevé du compteur d'eau d'appoint ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du niveau bas du bac ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Relevé des températures d'eau E/S ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du taux de déconcentration ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'état de propreté des surfaces ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Analyse d'eau pour recherche de LEGIONELLA (Opération réalisée par un prestataire) ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","[...] Renseignement du livret d'entretien  ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," "," ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","NOTA.: ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","Pour les installations soumises à autorisation recherche de légionelle mensuelle ",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR1M-OU","Tour Aéro-Réfrigérante ouverte"," ","Pour les installations soumises à déclaration recherche de légionelle bimestrille",0,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'état des packings et du circuit de pulvérisation ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'entartrage et de la corrosion du bac ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du système d'appoint d'eau ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du bon fonctionnement de la déconcentration automatique ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'intensité de la résistance antigel et du cordon chauffant ( voir gamme cordon chauffant ) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du delta P pompe de pulvérisation (tour à circuit fermé) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle du delta P batterie d'échange (tour à circuit fermé) ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'état de la tension des courroies ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'état de la protection mécanique du système de transmission ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'alignement des poulies ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle roulements et graissage paliers ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle des raccordements sur la boite à bornes du moteur ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de la fixation des volutes ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de l'état des plots antivibratiles ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de la fixation des appareils de mesure et des liaisons équipotentielles ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Contrôle de la cohérence des appareils de mesure ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Mesure et enregistrement des performances si nécessaire ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TAR-OU","Tour Aéro-Réfrigérante ouverte","TAR6M-OU R","Tour Aéro-Réfrigérante ouverte"," ","[...] Renseignement du livret d'entretien ",10,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-EG","Traitement réseau eau glycolée","TRE6M-EG","Traitement réseau eau glycolée"," ","[...] Contrôle du PH ( = 9 ) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-EG","Traitement réseau eau glycolée","TRE6M-EG","Traitement réseau eau glycolée"," ","[...] Relevé de la consommation en produit de traitement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-EG","Traitement réseau eau glycolée","TRE6M-EG","Traitement réseau eau glycolée"," ","[...] Contrôle et réglage, si nécessaire, de l'injection en produit de traitement (mg produit/litre d'appoint) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-EG","Traitement réseau eau glycolée","TRE6M-EG","Traitement réseau eau glycolée"," ","[...] Mesure de la protection antigel ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-EG","Traitement réseau eau glycolée","TRE6M-EG","Traitement réseau eau glycolée"," ","[...] Analyse physico-chimique de l'eau et des dépôts",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Contrôle du TH (=0°C) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Contrôle du PH (=9,5) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Contrôle teneur en sulfites ( >40 mg ) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Relevé de la consommation en produit de traitement ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Contrôle et réglage, si nécessaire, de l'injection en produit de traitement (mg produit/litre d'appoint) ",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","TRE-FE","Traitement réseau fermé","TRE3M-FE","Traitement réseau fermé"," ","[...] Analyse physico-chimique de l'eau (préconisation)",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA1A","Unité gainable"," ","Mesures: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA1A","Unité gainable"," ","[...] Mesure du débit global minimal d'air neuf de l'installation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA1A","Unité gainable"," ","[...] Mesure et enregistrement des performances",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle du bon fonctionnement du moteur de ventilation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle de l'intensité et de l'isolement de la batterie électrique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle  et essais des sécurités des batteries électrique ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Nettoyage du bac de récupération des condensats ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle de l'étanchéité des batteries ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle de l'état des soufflets et plots antivibratiles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle des liaisons équipotentielles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle des presse-étoupes ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle des vannes et servomoteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Nettoyage intérieur complet du caisson ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Nettoyage extérieur complet du caisson ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Remplacement des filtres si nécessaire ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," "," ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","Régulation: ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Dépoussiérage des cartes ou des régulateurs ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle serrage des connexions ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Vérification des points de consignes et paramètres de réglages ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","UGA","Unité gainable","UGA6M","Unité gainable"," ","[...] Contrôle de l'état de fonctionnement des actionneurs",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Contrôle de l'alimentation électrique ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Contrôle de l'état de la sparklet ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Contrôle du contact de fin de course et du report service de sécurité ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Contrôle des joints de scellement et des matériaux réfractaires ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Vérification du fonctionnement de la commande manuelle ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Contrôle de l'asservissement électrique du ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1A","Volet coupe feu"," ","[...] Enregistrement des essais et contrôles dans le registre de sécurité et sur BT préventif",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF1M","Volet coupe feu"," ","[...] Contrôle par simulation du bon fonctionnement des détecteurs et des fusibles",1,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF6M","Volet coupe feu"," ","[...] Contrôle de l'état des galets et des câbles des portes coulissantes ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF6M","Volet coupe feu"," ","[...] Nettoyage des rails et glissières ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF6M","Volet coupe feu"," ","[...] Vérification de la liberté de fonctionnement des dispositifs de fermeture ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF6M","Volet coupe feu"," ","[...] Vérification de l'absence d'obstacle sur le volet ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCF","Volet coupe feu","VCF6M","Volet coupe feu"," ","[...] Inspection des systèmes de détection et vérification des sources d'alimentation",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle des connexions électriques ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle et dépoussiérage du moto ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle et dépoussiérage des batteries ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle calorifuge et état extérieur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle du thermostat de sécurité ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO1A","Ventilo-convecteur"," ","[...] Contrôle de l' encombrement ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle de la disponibilité ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle du filtre et remplacement si nécessaire ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle du fonctionnement des commutateurs Chaud/Froid/Ventilateur ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle du bon fonctionnement de la régulation et des électrovannes ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle évacuation et pompe de relevage éventuelle ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Nettoyage du bac à condensât ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle du fonctionnement normal de la batterie électrique ",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VCO","Ventilo-convecteur","VCO6M","Ventilo-convecteur","Balisage de la zone de travail\nUtilisation de plateforme","[...] Contrôle du thermostat de sécurité",0.5,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'état général ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'état de la volute ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'état de la protection mécanique des courroies ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'état de la tension des courroies ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'alignement des poulies ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle des roulements et graissage des paliers ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle des raccordements sur la boite à bornes du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'intensité et de l'isolement du moteur de ventilation ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de la fixation de la volute et du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Contrôle de l'état des plots antivibratiles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-CE","Ventilateur centrifuge","VEN6M-CE","Ventilateur centrifuge"," ","[...] Nettoyage complet",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de l'état général ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de l'hélice et du jeu d'arbre ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle des roulements et graissage des paliers ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle des raccordements sur la boite à bornes du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de l'intensité et de l'isolement du moteur  ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de l'état de la cage ou des grilles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de la fixation du ventilateur et du moteur ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Contrôle de l'état des plots antivibratiles ",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VEN-HE","Ventilateur hélicoïdal","VEN6M-HE","Ventilateur hélicoïdal","ATTENTION :\n\nCONSIGNATION ELECTRIQUE ET MECANIQUE OBLIGATOIRE","[...] Nettoyage complet",2,5]
["CVCD","Chauf - Ventil - Clim - Desenf","VRV","VRV"]
["DIV","Divers","CPT-EN","Compteur d'energie"]
["DIV","Divers","CPT-GA","Compteur Gaz"]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","[...] Contrôle de l'état des supports, de la cuve et des tuyauteries (corrosion, revêtement) ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","[...] Contrôle du fonctionnement des détecteurs de fuite et des reports d'alarme ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","[...] Contrôle des limiteurs de remplissage ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","[...] Vérification de la jauge de remplissage ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","[...] Contrôle de la date de ré-épreuve du réservoir ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," "," ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","NOTA: ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","  - Réservoir à simple paroi en fosse : 1er renouvellement : 25 ans Maxi après date de mise en service & Renouvellements suivants : 5 ans ",2,5]
["DIV","Divers","CUV","Cuve à fuel","CUV1A","Cuve à fuel"," ","  - Réservoir enterré à simple enveloppe en contact avec le sol :1er renouvellement : 15 ans Maxi après date de mise en service & Renouvellements suivants : 5 ans",2,5]
["DIV","Divers","PLG","Poste de livraison gaz","PLG6M","Poste de livraison gaz"," ","[...] Contrôle de l'étanchéité du circuit ",1,5]
["DIV","Divers","PLG","Poste de livraison gaz","PLG6M","Poste de livraison gaz"," ","[...] Man&#156;uvre des vannes (hormis la vanne de barrage gaz) ",1,5]
["DIV","Divers","PLG","Poste de livraison gaz","PLG6M","Poste de livraison gaz"," ","[...] Contrôle de l'état des supports et des tuyauteries (corrosion, revêtement)",1,5]
["DIV","Divers","PLG","Poste de livraison gaz","REG1A","Reseau gaz"," ","[...] Contrôle du reseau gaz",2,5]
["DIV","Divers","ROND","Ronde technique"]
["DIV","Divers","SECHVX","Séche Cheveux","SECHVX1A","Visite Annuelle Séche Cheveux"," ","[...] Démontage séche cheveux ",0.4,5]
["DIV","Divers","SECHVX","Séche Cheveux","SECHVX1A","Visite Annuelle Séche Cheveux"," ","[...] Nettoyage séche cheveux ",0.4,5]
["DIV","Divers","SECHVX","Séche Cheveux","SECHVX1A","Visite Annuelle Séche Cheveux"," ","[...] Remontage séche cheveux",0.4,5]
["GMAO","GMAO","GMAO","GMAO"]
["HQE","HQE","DECH","Reporting dechets","DECH1A","Reporting des déchets"," ","Opération sous traitée ",2,5]
["HQE","HQE","DECH","Reporting dechets","DECH1A","Reporting des déchets"," ","Recuperation des données du prestataire.",2,5]
["HQE","HQE","DERA","Deratisation","DERA1A","Deratisation"," ","Opération sous traitée",0.2,5]
["HQE","HQE","ENV","Espace vert et terrasse","ENV1A","NETTOYAGE DE LA TERRASSE"," ","Nettoyage de la terrasse",2,5]
["HQE","HQE","ENV","Espace vert et terrasse","ENV1M","Espace vert et terrasse"," ","Opération sous traitée ",0]
["HQE","HQE","ENV","Espace vert et terrasse","ENV1M","Espace vert et terrasse"," ","Vérification de la prestation",0]
["HQE","HQE","ENV","Espace vert et terrasse","ENV1M","Espace vert et terrasse"," ","Opération sous traitée ",5,5]
["HQE","HQE","ENV","Espace vert et terrasse","ENV1M","Espace vert et terrasse"," ","Vérification de la prestation",5,5]
["HQE","HQE","ENV","Espace vert et terrasse","ENV3M","Entretien toiture mur végétale"," ","Contrôle de la prestation",1,5]
["HQE","HQE","NEW","Newsletter","NEW1M","Newsletter consommation"," ","Envoyer la newsletter par courriel au Porteur de la certification pour renvoie au(x) locataire(s). ",1,5]
["HQE","HQE","NEW","Newsletter","NEW1M","Newsletter consommation"," "," ",1,5]
["HQE","HQE","NEW","Newsletter","NEW1M","Newsletter consommation"," ","Newsletter intégrée au Rapport d'activité.",1,5]
["HQE","HQE","PPM","Analyse d'air","ppm1A","Analyse d'air"," ","[&#133;] Analyse d'air conforme ",3,5]
["HQE","HQE","PPM","Analyse d'air","ppm1A","Analyse d'air"," ","[&#133;] Annexer le rapport d'analyse a la gamme",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Réunion mensuelle entre le Porteur de la Certification et le Responsable d'exploitation pour vérification de l'ensemble du processus HQE sur site.  ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," "," ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Vérification des indicateurs environnementaux ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Vérification des rapports  ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Vérification des analyses énergétiques ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Vérification de l'atteinte des objectifs ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," "," ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Revue du Système de management de l'exploitation ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," "," ",3,5]
["HQE","HQE","REV","Revu d'exploitation","REV1M","Revue d'exploitation"," ","Effectuer un compte rendu.",3,5]
["INDUST","Industriel","AUG","Arret d'urgence gare"]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle de la présence du schéma dans l'armoire électrique.Remise à jour du schéma si nécessaire ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Essai Auto/Arrêt/Manu ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Essai arrêt d'urgence ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Suivi de la procédure de consignation  ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle connexions et bruits et fixations des relais ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Essai des reports et télécommandes GTB ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle du serrage des connexions ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle du calibrage des fusibles par rapport au schéma ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle du réglage des relais thermiques par rapport au schéma ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle des temporisations ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle état des goulottes ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle état des presse-étoupes ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Contrôle fixation du coffret ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Nettoyage et dépoussiérage ",0.5,5]
["INDUST","Industriel","CEC","Coffret Elec Chaine","COF1A","Coffret électrique"," ","[...] Suivi de la procédure de déconsignation",0.5,5]
["INDUST","Industriel","CFC","Contact fin de course"]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Vidange des moto-Réducteurs (tous les 2 ans) ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Graissage et réglages du jeu des chaînes et pignons ( remplacement si nécessaire) ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôle et réglage du jeu et de la tension des bandes de transport ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôle de l'isolement des moteurs ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôle du serrage des plaques à bornes moteurs ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôler les raccords pneumatiques ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôler les connectique sur les cellules, les lecteurs et décodeurs ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôler les vérins et biellette ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Vidanger les impuretée dans les cuves d'air ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôler les galets et roulements ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Dépoussierrage et graissage de l'ensemble des organes ",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA1A","Convoyeur chaine annuelle"," ","[...] Contrôle des fixations du relevable ( si éxistant )",40,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle et réglage de la tension des chaînes et graissage si nécessaire ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle et réglage de la tension des bandes ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle de l'état des bandes de transport(si existant) ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle de l'état des courroies d'entraînement des rouleaux ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôler l'état des rouleaux ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Evacuation des déchets dans la cuve transparente ( Air Comprimé) ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle des galets et des ressorts ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôle des cellules ",2,5]
["INDUST","Industriel","CONV","Convoyeur à chaine","CCHA3M","Convoyeur chaine trimestrielle"," ","[...] Contrôler l'absence de bruit anormal",2,5]
["INDUST","Industriel","DEC","Decodeur"]
["INDUST","Industriel","ECA","Ensemble capteur"]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôle de l'état général ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Consigner l'armoire électrique ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôle de serrage et nettoyage de l'armoire ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Déconsigner l'armoire électrique ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Relever l'intensité (comparer à l'intensité plaquée) ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Nettoyage interne à l'aspirateur de la tête à souder ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôler l'état des courroies ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôler les sécurités ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôler la qualité d'aspiration ",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1M","Cercleuse Mensuelle"," ","[&#8230;] Contrôler la qualité de cerclage",1,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Maintenance constructeur ponctuelle selon accord du client ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Contrôler l'état du galet de lancement ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Nettoyage des lames de chauffe ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Vérification et remplacement si besoin des courroies ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Graissage des engrenages ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Contrôle de la sécurité ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Contrôler l'efficacité de l'aspiration ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Contrôler le bon fonctionnement du cerclage sur un carton ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Remplir une feuille d'appréciation ",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER6M","Cercleuse Semestrielle"," ","[&#8230;] Classer le bon d'intervention du sous-traitant",4,5]
["INDUST","Industriel","EMB","Nécessaire d'emballage","CER1A","Cercleuse Annuelle"," ","[&#8230;] Remplacement du galet de lancement",1,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle et réglage de la tension des chaînes et graissage si nécessaire ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle et réglage de la tension des bandes ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle de l'état des bandes de transport(si existant) ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle de l'état des courroies d'entraînement des rouleaux ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler l'état des rouleaux ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler l'absence de bruit anormal ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle des galets et des ressorts ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle des cellules ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle de la table élévatrice ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôle des vérins ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler le lecteur ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler le fonctionnement des sécurités ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler l'intensité sur les moto-réducteur ",2,5]
["INDUST","Industriel","GARE","Gare","GARE3M","Gare Trimestrielle"," ","[...] Contrôler le réglage de la protection thermique",2,5]
["INDUST","Industriel","LCB","Lecteur Code Barre","LCB2M","Lecteur Code Barre Bimestriell"," ","[&#8230;] Nettoyage des glaces sur les lecteurs ",1,5]
["INDUST","Industriel","LCB","Lecteur Code Barre","LCB2M","Lecteur Code Barre Bimestriell"," ","[&#8230;] Contrôle de la fixation ",1,5]
["INDUST","Industriel","LCB","Lecteur Code Barre","LCB2M","Lecteur Code Barre Bimestriell"," ","[&#8230;] Contrôler le bon fonctionnement",1,5]
["INDUST","Industriel","MOT-RED","Moto Reducteur"]
["INDUST","Industriel","RACK","Rack","RACK1M","Rack Mensuelle"," ","[&#8230;] Faire un contrôle visuel des racks et signaler toute anomalie au responsable magasin",1,5]
["INDUST","Industriel","RACK","Rack","RACK1A","Contrôle RACK"," ","Opération réalisée par un organisme agrée",2,5]
["INDUST","Industriel","SYS-CONV","Système de convoyage"]
["LABO","Matériels de laboratoire","FILT","Filtration absolue","FIL1A-ABS","Filtration absolue","Appliquer la procédure d'habillage en ZAC","[&#133;] Appliquer la procédure DT site ",2,5]
["LABO","Matériels de laboratoire","FILT","Filtration absolue","FIL1A-ABS","Filtration absolue","Appliquer la procédure d'habillage en ZAC","[&#133;] Contrôle par photomètre de l'integritée des filtres en ZAC ",2,5]
["LABO","Matériels de laboratoire","FILT","Filtration absolue","FIL1A-ABS","Filtration absolue","Appliquer la procédure d'habillage en ZAC","[&#133;] Contrôle du TRH? ça c pour moi a verifier(taux de renouvellement d'air) ",2,5]
["LABO","Matériels de laboratoire","FILT","Filtration absolue","FIL1A-ABS","Filtration absolue","Appliquer la procédure d'habillage en ZAC","[&#133;] Contrôle des vitesses d'air par filtres en ZAC",2,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","Opération réalisée par un prestataire: ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique"," ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Nettoyage des menbranes(Selon besoin) ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Remplacement des filtres 10µm ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Remplacement des filtres charbon ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Remplacement des filtres 1µm ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Remplacement des filtres 0.22µm sur boucle ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Remplacement du filtre event sur cuve de stockage EPU ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Vérifier la programmation de l'adoucisseur ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Nettoyage de la chambre de mesure testomat ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Changement des joints du testomat ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Vérification de la sonde PH, remplacement si besoin ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Vérification des sondes de conductivité, remplacement si besoin ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Contrôle de la pompe d'njection soude ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Desinfection du prétraitement selon procédure ",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM1A","Osmoseur","Port des EPI\nRisque chimique","[...] Desinfection de la boucle selon procédure",8,5]
["LABO","Matériels de laboratoire","OSM","Osmoseur","OSM2M","OSMOSEUR"," ",null,2,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Visualisation de l'écoulement d'air dans l'ouverture par fumigène ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Mesurage de la vitesse d'air dans l'ouverture selon méthode et valeurs de référence figurant dans la fiche d'instructions de chaque équipement (valeurs établies à la réception) ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Contrôle du fonctionnement de l'indicateur de débit et de son alarme ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Inspection après démontage du mécanisme de manœuvre d'écran ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Vérification des butées d'arrêt de l'écran et de leur alarme ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Nettoyage du plenum d'extraction après démontage de la aparoi verticale arrière  ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Vérification du laveur d'air au rejet si la sorbonne en est équipée ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Remplacement de l'élément épurateur au rejet si la sorbonne en est équipée ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Examen visuel du conduite de rejet et de ses accessoires ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Inspection du ventilateur d'extraction (pales, vitesse et sens de rotation du ventilateur) ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Inspection des organes de distribution des énergies et des fluides ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Contrôle du système de ventilation de compensation du local selon plan de contrôle et de maintenance approprié ",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR1A","Sorbonne","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","[…]Consignation des interventions dans le livret d'entretien de la sorbonne.",4,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR3M","SORBONNES","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","Maintenance préventive, corrective et conditionnelle, niveaux 1 à 3 de la norme FDX 60-000 pour les équipements d'Extraction d'Air de type : SORBONNES ",2,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR3M","SORBONNES","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","&#8226; RESEAU IRIAN LAB ",2,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR3M","SORBONNES","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","o Vérification du paramétrage et de la bonne réponse des éléments de régulation. ",2,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR3M","SORBONNES","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","o Contrôles du superviseur, des capteurs et des alarmes. ",2,5]
["LABO","Matériels de laboratoire","SORB","SORBONNE","SOR3M","SORBONNES","&#8226; NF EN 14175\n&#8226; TS 14175-5\n&#8226; XP X 15-203 et 15-206 de janvier 2005\n&#8226; articles R 4222-1 à 25, R 4412-149 et 150, R4722-1,-2,-13,-14 et -26 fixant les règles générales que doivent respecter les employeurs (décret n°84-1093 du 7 décembre 1984)\n&#8226; article R 4222-20 et -21\n&#8226; arrêté du 8 octobre 1987","o Vérification des BUS de communication.",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle des organes de sécurité(boucle de détection et cellules photoélectriques) ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Nettoyage des cellules photoélectriques ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Vérification du bon fonctionnement du dispositif de débrayage manuel ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle des éléments de transmission du mouvement (bras articulés, câbles, chaînes, courroies,&#133;) ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Lubrification et réglages nécessaires au bon fonctionnement ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle de l'opérateur (moto réducteur électrique, opérateur électro-hydraulique,&#133;) ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle et resserrage des connexions électriques  ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle de la fixation barrières au sol ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle de l'état des peintures et de la corrosion ",2,5]
["PAU","Portes automatiques","BAU","Barrière automatique","BAU6M","Barrière automatique"," ","[...] Contrôle des organes de commande et de télécommande.Nettoyage des lecteurs",2,5]
["PAU","Portes automatiques","PAU-GR","Grille motorisée"]
["PAU","Portes automatiques","PAU-PM","Porte motorisée"]
["PAU","Portes automatiques","PAU-PO","Portillons"]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","Opération réalisée par un prestataire: ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," "," ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle du bon fonctionnement et de l'état de la signalisation (feux orange, clignotants, éclairage)  ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle de l'état de la signalisation  au sol de l'aire dangereuse de mouvement ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle du bon fonctionnement des dispositifs de sécurité des personnes (lames palpeuses, pressostats, cellules photoélectriques,&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Nettoyage des cellules de réflexion ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Vérification du bon fonctionnement du dispositif de débrayage manuel, du limiteur d'effort ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle de la présence de la procédure de dépannage ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des articulations (charnières, pivots&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des cycles de fonctionnement dans les zones d'accostage ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des éléments de transmission du mouvement (bras articulés, câbles, chaînes, courroies,&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Lubrification et réglages nécessaires au bon fonctionnement ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle de l'opérateur (moto réducteur électrique, opérateur électro-hydraulique,&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des éléments de guidage (rails, galets&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des articulations (charnières, pivots&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des fixations ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des systèmes d'équilibrage (contrepoids, ressorts&#133;) ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle du fonctionnement du système empêchant la chute du tablier ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle de la temporisation ouverture / fermeture ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle de l'état des peintures et de la corrosion ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Contrôle des organes de commande et de télécommande.Nettoyage des lecteurs ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Examen général du fonctionnement de la porte ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Remise d'un rapport à chaque fin de visite  ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Renseignement du livret d'entretien porte et registre de sécurité ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Relevé de l&#146;intensité du moteur ",1,5]
["PAU","Portes automatiques","PAU-SE","Porte automatique sectionnelle","PAU6M-SE","Porte automatique sectionnelle"," ","[...] Relevé de l&#146;isolement du moteur",1,5]
["PAU","Portes automatiques","PAU-TO","Tourniquet avec Accès Cont."]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Contrôle des glissières.Graissage si nécessaire. ",1,5]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Controle et graissage des chaînes si nécessaire. ",1,5]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Réglage de la tension des chaînes ",1,5]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Contrôle de réducteurs (niveaux) ",1,5]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Vérification de fonctionnement ",1,5]
["PAU","Portes automatiques","RID","Rideau métallique","RID6M","Rideau métallique"," ","[...] Réglage des fins de course",1,5]
["PHE","Propreté Hygiène Surface","PHS","Propreté hygiène surface"]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","Bac à saumure: ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Nettoyage de la vanne, de la canne d'aspiration et de la crépine ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Nettoyage du bac à saumure ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Contrôle du niveau de sel ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Contrôle du stock de sel ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," "," ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Resserrage des presse-étoupes ",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1A","Adoucisseur"," ","[...] Contrôle des connexions électriques",2,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1S","Adoucisseur"," ","Analyses d'eau: ",0.1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1S","Adoucisseur"," ","[...] Contrôle du niveau de sel ",0.1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1S","Adoucisseur"," ","[...] Analyse TH, en sortie d'adoucisseur<2°f ",0.1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO1S","Adoucisseur"," ","[...] Analyse TH, après mixage",0.1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","Adoucisseur ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Contrôle de la programmation de l'horloge ( Heure, Fréquence ) ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Contrôle du fonctionnement de l'électrovanne pilote ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Manœuvre de la robinetterie ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Contrôle des clapets ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Contrôle de la bonne régénération de l'adoucisseur (Régénération manuelle) ",1,5]
["PLOM","Plomberie","ADO","Adoucisseur","ADO6M","Adoucisseur"," ","[...] Contrôle du bon écoulement des eaux",1,5]
["PLOM","Plomberie","ANALYSE","Analyse Legionelle","ANA3M","Analyse Legionelle"," ","\"[&#8230;] Opération sous traitée",0.3,5]
["PLOM","Plomberie","ARRO","Système d'arrosage"]
["PLOM","Plomberie","ATA","Anti-tartre"]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG1A","Bac à  graisse"," ","Opération réalisée par un prestataire: ",1,5]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG1A","Bac à  graisse"," "," ",1,5]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG1A","Bac à  graisse"," ","Curage annuel  des canalisations horizontales par les regards",1,5]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG6M","Bac à  graisse"," ","Opération réalisée par un prestataire: ",1,5]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG6M","Bac à  graisse"," "," ",1,5]
["PLOM","Plomberie","BAG","Bac à  graisse","BAG6M","Bac à  graisse"," ","Pompage et nettoyage bac à graisses et fécules (Selon besoin)",1,5]
["PLOM","Plomberie","BEC-GE","Ballon EC Elec >200L -Centrale"]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du thermostat de régulation ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du thermostat de sécurité ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle aération  haute et basse ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," "," ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","Brûleur: ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Couper le courant sur le coupe circuit, fermer le robinet de barrage gaz ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Déconnecter l'arrivée gaz, les fils électriques du bloc de régulation et la dérivation du thermocouple ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Tirez le brûleur horizontalement ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du bon état des rampes ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du bon état des injecteurs ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle de la veilleuse et du bon état de la bougie d'allumage ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Nettoyage du thermocouple ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du bon fonctionnement de l'allumeur piézo ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle de l'étanchéité gaz ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du bon fonctionnement de la veilleuse après remise en service ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," "," ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","Conduit gaz: ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Nettoyage intérieur du conduit gaz ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Nettoyage intérieur du coupe tirage ",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1A-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle de l'étanchéité",4,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1M-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle absence de fuite ",0.5,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1M-GG","Ballon ECS Gaz>200L (central)"," ","[...] Contrôle du bon fonctionnement de la soupape de sûreté ",0.5,5]
["PLOM","Plomberie","BEC-GG","Ballon EC Gaz >200L - Centrale","BEC1M-GG","Ballon ECS Gaz>200L (central)"," ","[...] Chasse par la vanne de vidange pour éliminer les éventuelles boues",0.5,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","[...] *Vidange du ballon et contrôle des parois internes ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","[...] Contrôle et détartrage des faisceaux ou des résistances électrique ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","[...] Remplacement de l'anode (Tous les 2 ans) ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","[...] Nettoyage interne et désinfection chimique du ballon (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","[...] Analyse légionelle en fond de ballon (Préconisation) (opération réalisée par un prestataire) ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," "," ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1A-PE","Ballon ECS Elec<200L (local)"," ","NOTA.: *Si les parois présentent des signes de corosion importante prévoir la remise en état du ballon ou son remplacement",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC6M-PE","Ballon ECS Elec<200L (local)"," ","A Faire",0.5,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1M-PE","Ballon ECS carnet sanitaire"," ","[…] Manœuvre des systèmes de sécurité(cf procédure 5.5.2) ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1M-PE","Ballon ECS carnet sanitaire"," ","[…] Véfication des organes de régulation(cf procédure 5.5.8) ",1,5]
["PLOM","Plomberie","BEC-PE","Ballon EC Elec < 200L - Locale","BEC1M-PE","Ballon ECS carnet sanitaire"," ","[…] Contrôle de la soupape de sécurité",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","Lavabos: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","[...] Analyse bactériologique et légionelle ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","Nota.: (Préconisation) Sur échantillonage, points d'usages les plus éloignés ou peu utilisés ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," "," ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","Douches: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","[...] Analyse légionelle (Semestriel pour les ERP) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","[...] Remplacer les éléments périphériques de distribution (ioints,filtres de robinet, pommes et flexibles de douches) en fonction de leur étât d'usure. ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","[...] Détartrage des pommes de douches dans une solution à Ph acide telle que: Acide sulfamique ; Vinaigre blanc pendant 15 mn (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1A","Bloc sanitaire"," ","[...] Rinçage puis désinfection dans une solution chlorée contenant au moins 50 mg/L de chlore libre (13 ml d'eau de Javel dans 10 litres d'eau) pendant 30 minutes avant repose (Si nécéssaire)",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1M","Bloc sanitaire"," ","[...] Contrôle absence de fuite ",0,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1M","Bloc sanitaire"," ","[...] Contrôle de l'écoulement des lavabos, urinoirs, WC ",0,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1M","Bloc sanitaire"," ","[...] Contrôle de l'état de la robinetterie, mousseurs, mobilier sanitaire ",0,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA1M","Bloc sanitaire"," ","[...] Contrôle de l'éclairage",0,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","Lavabos: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle absence de fuite ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle du mécanisme de la bonde ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Manœuvre et contrôle des vannes d'isolement ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle du fonctionnement séchoir à main ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Détartrage des mousseurs dans une solution à Ph acide telle que: Acide sulfamique ; Vinaigre blanc pendant 15 mn (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Rinçage puis désinfection des mousseurs dans une solution chlorée contenant au moins 50 mg/L de chlore libre (13 ml d'eau de Javel dans 10 litres d'eau) pendant 30 minutes avant repose (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," "," ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","WC: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle absence de fuite ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle du robinet d'arrêt ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle de l'écoulement WC  ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle état et fixation abattant WC ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle du bon fonctionnement de la chasse d'eau WC ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA6M","Bloc sanitaire"," ","[...] Contrôle du bon fonctionnement du mécanisme d'eau",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","Lavabos: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle absence de fuite ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle du mécanisme de la bonde ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Manoeuvre et contrôle des vannes d'isolement ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle du fonctionnement séchoir à main ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Détartrage des mousseurs dans une solution à Ph acide telle que: Acide sulfamique ; Vinaigre blanc pendant 15 mn (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Rinçage puis désinfection des mousseurs dans une solution chlorée contenant au moins 50 mg/L de chlore libre (13 ml d'eau de Javel dans 10 litres d'eau) pendant 30 minutes avant repose (Si nécéssaire) ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," "," ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","WC: ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle absence de fuite ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle du robinet d'arrêt ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle de l'écoulement WC  ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle état et fixation abattant WC ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle du bon fonctionnement de la chasse d'eau WC ",1,5]
["PLOM","Plomberie","BSA","Bloc sanitaire","BSA3M","Blocs Sanitaire"," ","[...] Contrôle du bon fonctionnement du mécanisme d'eau",1,5]
["PLOM","Plomberie","CPT-EA","Compteur d'eau"]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","Opération réalisée par un prestataire: ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," "," ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Contrôle de la pression et du débit de fuite de la vanne amont ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Contrôle de l'obturateur et de la membrane ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Contrôle du fonctionnement de la soupape ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Contrôle de la pression et du débit de fuite ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Contrôle des différentiels de pression ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","[...] Transmission à la DASS de la fiche de contrôle N°3 instruite par le technicien ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," "," ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS1A","Disconnecteur"," ","NOTA.: Circulaires des 09/08/78 et 10/04/87,  Le contrôle doit être effectué par un technicien habilité",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","- Vérifier que la protection est toujours adaptée au risque ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","- Vérifier que l'installation du disconnecteur est toujours conforme ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","- Vérifier : ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· la facilité d'accès à l'ensemble de protection ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· l'aération du local ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· la non inondabilité du site ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· la manoeuvre aisée des éléments de l'ensemble de protection ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· le dégagement autour de l'ensemble de protection ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· la position des orifices de décharge ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· l'état de surface de l'ensemble de protection ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· la capacité d'évacuation des réseaux collecteurs des eaux de rejet ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","· l'existence des couleurs conventionnelles et des pictogrammes caractéristiques ",2,5]
["PLOM","Plomberie","DIS","Disconnecteur","DIS6M","Disconnecteur"," ","- Nettoyer le filtre",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV1A","Réseaux Eau de Ville"," ","[...] Contrôle de l'état des tuyauteries après démontage des manchettes témoins ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV1A","Réseaux Eau de Ville"," ","[...] Rinçage des bypasses",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Contrôle des filtres ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Contrôle de l'état externe des canalisations ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Contrôle du bon fonctionnement détendeurs, réducteurs de pression ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Contrôle des anti béliers ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Chasses sur l'ensemble des points bas et sur les points d'usage à faibles débits ",2,5]
["PLOM","Plomberie","EDV","Réseaux Eau de Ville","EDV3M","Réseaux Eau de Ville"," ","[...] Analyse physico-chimique (préconisation)",2,5]
["PLOM","Plomberie","EVA","Réseaux d'évacuations EU/EV/EP","EVA1A","Réseaux d'évacuations EU/EV/EP"," ","[...] Contrôle de l'étanchéité des joints, absence de fuite ",4,5]
["PLOM","Plomberie","EVA","Réseaux d'évacuations EU/EV/EP","EVA1A","Réseaux d'évacuations EU/EV/EP"," ","[...] Nettoyage des regards et siphons de sol ",4,5]
["PLOM","Plomberie","EVA","Réseaux d'évacuations EU/EV/EP","EVA1A","Réseaux d'évacuations EU/EV/EP"," ","[...] Contrôle du bon écoulement des eaux",4,5]
["PLOM","Plomberie","FIL-TA","Filtre à tamis","FIL1A-TA","Filtre à tamis"," ","[...] Nettoyage du tamis (Selon la perte de charge) ",2,5]
["PLOM","Plomberie","FIL-TA","Filtre à tamis","FIL1A-TA","Filtre à tamis"," ","[...] Contrôle des joints de brides et remplacement si nécessaire",2,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Contrôle de l'étanchéité du clapet de refoulement ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Contrôle de l'état de l'accouplement ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Contrôle de la boite à bornes du moteur ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Contrôle de l'intensité absorbé et de l'isolement du moteur ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Nettoyage de la roue et de la crépine ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Contrôle de l'état du manchon de refoulement ou du raccord souple ",4,5]
["PLOM","Plomberie","FOS","Fosse de relevage","FOS1A","Fosse de relevage"," ","[...] Nettoyage complet du puisard et pompage de la fosse de relevage (Opération réalisée selon besoin par un prestataire)",4,5]
["PLOM","Plomberie","HYD","Séparateur d'hydrocarbure","HYD1A","Séparateur d'hydrocarbure"," ","Opération réalisée par un prestataire: ",2,5]
["PLOM","Plomberie","HYD","Séparateur d'hydrocarbure","HYD1A","Séparateur d'hydrocarbure"," "," ",2,5]
["PLOM","Plomberie","HYD","Séparateur d'hydrocarbure","HYD1A","Séparateur d'hydrocarbure"," ","[...] Vidange et nettoyage selon capacité (Selon besoin) ",2,5]
["PLOM","Plomberie","HYD","Séparateur d'hydrocarbure","HYD1A","Séparateur d'hydrocarbure"," ","[...] Destruction des hydrocarbures (Selon besoin)",2,5]
["PLOM","Plomberie","NPC","NOURRICE"]
["PLOM","Plomberie","PAB","POT A BOUE"]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Contrôle de la programmation de l'injection ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Contrôle du bon fonctionnement de l'électrovanne pilote ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Nettoyage de la vanne, de la canne d'aspiration et de la crépine ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Man&#156;uvre de la robinetterie ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Contrôle des clapets d'aspiration et de refoulement ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Resserrage des presse-étoupes et réfection si nécessaire ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Contrôle des connexions électriques ",2,5]
["PLOM","Plomberie","PDO","Pompe doseuse","PDO6M","Pompe doseuse"," ","[...] Nettoyage du bac",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle de l'absence de fuite au niveau des garnitures ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Relevé de l'intensité absorbée et de l'isolement du moteur ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle des liaisons équipotentielles de masse ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Relevé des pressions amont / aval et calcul du Delta P ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle des roulements ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle de l'alignement du moteur et de la pompe ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle de la fixation et des supports antivibratiles ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Permutation des pompes selon temps de fonctionnement ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle de l'état de l'accouplement et de sa protection mécanique (uniquement sur une pompe avec accouplement) ",2,5]
["PLOM","Plomberie","PPE","Pompe de Circulation","PPE6M","Pompe de Circulation"," ","[...] Contrôle du fonctionnement du clapet (uniquement sur une pompe double)",2,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Contrôle de l'étanchéité du clapet de refoulement ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Contrôle de l'état de l'accouplement ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Contrôle de la boite à bornes du moteur ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Contrôle de l'intensité absorbé et de l'isolement du moteur ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Nettoyage de la roue et de la crépine ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Contrôle de l'état du manchon de refoulement ou du raccord souple ",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR1A","Pompe de relevage"," ","[...] Nettoyage complet du puisard et pompage de la fosse de relevage (Opération réalisée selon besoin par un prestataire)",4,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR6M","Pompe de relevage"," ","[...] Contrôle du bon fonctionnement des flotteurs et de ses asservissements  ",0.5,5]
["PLOM","Plomberie","PPR","Pompe de relevage","PPR6M","Pompe de relevage"," ","[...] Essai des séquences de démarrage et de mise en sécurité",0.5,5]
["PLOM","Plomberie","PRE-EL","Préparateur  ECS","PRE6M-EL","Préparateur ECS"," ","[...] Contrôle de l'absence de fuite ",2,5]
["PLOM","Plomberie","PRE-EL","Préparateur  ECS","PRE6M-EL","Préparateur ECS"," ","[...] Contrôle du point de consigne (<55°C) ",2,5]
["PLOM","Plomberie","PRE-EL","Préparateur  ECS","PRE6M-EL","Préparateur ECS"," ","[...] Contrôle de la fixation de l'appareil ",2,5]
["PLOM","Plomberie","PRE-EL","Préparateur  ECS","PRE6M-EL","Préparateur ECS"," ","[...] Remplacement des joints (selon besoin) ",2,5]
["PLOM","Plomberie","PRE-EL","Préparateur  ECS","PRE6M-EL","Préparateur ECS"," ","[...] Remplacement de la cartouche thermostatique (selon besoin)",2,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle de l'absence de fuite ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des manchons de dilatation (recommandation des constructeurs: -Ne pas peindre les manchon et prévoir le remplacement tout les 10 ans ) ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des débits sur vannes de réglage (utilisation de la mallette)  ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des thermomètres et des manomètres ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des purgeurs ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des filtres ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle du calorifuge ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle du collecteur des réseaux de récupération de purges ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des pots à boues et évacuations des boues par chasse rapide  ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Contrôle des supports de tuyauterie ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Retouche de peinture  ",8,5]
["PLOM","Plomberie","REH","Réseau hydraulique","REH1A","Réseau hydraulique"," ","[...] Manoeuvres des vannes et contrôle de l'ensemble du réseau",8,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle du pressostat de commande ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Relevé des pressions de fonctionnement ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle des pressions d'asservissement ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de la boite à bornes moteur ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de l'intensité moteur ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de l'isolement et des liaisons équipotentielles ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Dépoussiérage du ventilateur de refroidissement du moteur ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle des roulements et graissage éventuel ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de l'accouplement ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de la protection mécanique des parties tournantes ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle de la fixation de l'ensemble et des plots antivibratiles ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle du filtre à tamis et nettoyage éventuel ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Contrôle du fonctionnement du clapet anti-retour ",2,5]
["PLOM","Plomberie","SUR","Surpresseur ","SUR6M","Surpresseur "," ","[...] Essai du basculement automatique P1/P2",2,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Contrôle du TH ( = 0°C ) ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Contrôle du PH ( 8,5 < PH < 9,3 ) ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Contrôle du taux de concentration ( < 3 ) ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Relevé de la consommation en produit de traitement ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Contrôle et réglage ,si nécessaire, de l'injection en produit de traitement (mg produit/litre d'appoint) ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Injection ponctuelle, si nécessaire, d'un produit de traitement bactéricide et algicide ",1,5]
["PLOM","Plomberie","TRE-OU","Traitement réseau ouvert","TRE3M-OU","Traitement réseau ouvert"," ","[...] Analyse physico-chimique de l'eau ",1,5]
["PLOM","Plomberie","VG","Vanne guillotine"]
["RMA","Rapport d'activité","RAPPORT","RAPPORT"]
["SECO","Second Oeuvre","FEN","Fenêtre","FEN1A","Fenêtre"," ","[...] Contrôle de l'aspect général  ",0.1,5]
["SECO","Second Oeuvre","FEN","Fenêtre","FEN1A","Fenêtre"," ","[...] Contrôle des joints d'étanchéité ",0.1,5]
["SECO","Second Oeuvre","FEN","Fenêtre","FEN1A","Fenêtre"," ","[...] Vérification des fixations ",0.1,5]
["SECO","Second Oeuvre","FEN","Fenêtre","FEN1A","Fenêtre"," ","[...] Contrôle des crémones et serrureries ",0.1,5]
["SECO","Second Oeuvre","FEN","Fenêtre","FEN1A","Fenêtre"," ","[...] Lubrification des parties mécaniques",0.1,5]
["SECO","Second Oeuvre","MAR","Mobilier armoire","MAR1A","Mobilier armoire"," ","[...] Ouverture fermeture des portes ",0.1,5]
["SECO","Second Oeuvre","MAR","Mobilier armoire","MAR1A","Mobilier armoire"," ","[...] Contrôle des glissières ",0.1,5]
["SECO","Second Oeuvre","MAR","Mobilier armoire","MAR1A","Mobilier armoire"," ","[...] Contrôle des serrures ",0.1,5]
["SECO","Second Oeuvre","MAR","Mobilier armoire","MAR1A","Mobilier armoire"," ","[...] Contrôle de la stabilité de l'armoire",0.1,5]
["SECO","Second Oeuvre","MBU","Mobilier bureau","MBU1A","Mobilier bureau"," ","[...] Ouverture et fermeture des tiroirs ",0.1,5]
["SECO","Second Oeuvre","MBU","Mobilier bureau","MBU1A","Mobilier bureau"," ","[...] Contrôle des pieds de bureaux ",0.1,5]
["SECO","Second Oeuvre","MBU","Mobilier bureau","MBU1A","Mobilier bureau"," ","[...] Contrôle des serrures ",0.1,5]
["SECO","Second Oeuvre","MBU","Mobilier bureau","MBU1A","Mobilier bureau"," ","[...] Contrôle de la fixation et ancrage ",0.1,5]
["SECO","Second Oeuvre","MBU","Mobilier bureau","MBU1A","Mobilier bureau"," ","[...] Contrôle de la stabilité du bureau",0.1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Contrôle de l'alimentation électrique ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Contrôle de l'état de la sparklet ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Contrôle du contact de fin de course et du report service de sécurité ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Contrôle des joints de scellement et des matériaux réfractaires ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Vérification du fonctionnement de la commande manuelle ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Contrôle de l'asservissement électrique du ventilateur ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1A","Porte coupe feu"," ","[...] Enregistrement des essais et contrôles dans le registre de sécurité et sur BT préventif",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Inspection technique ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Contrôle du bon fonctionnement des P.C.F ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","      - essai en manuel  ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","      - essai par simulation du fonctionnement des organes de détection ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Contrôle de l'état des galets et de l'ensemble câbles-poulies ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Nettoyage des rails et glissières ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Vérification de la liberté de fonctionnement des dispositifs de fermeture ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Vérification de l'absence d'objet sous la porte ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Inspection des systèmes de détection (voir chapitre \"Système de sécurité incendie\") ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF1M","Porte coupe feu"," ","[...] Contrôle par simulation du bon fonctionnement des détecteurs et des fusibles",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF6M","Porte coupe feu"," ","[...] Contrôle de l'état des galets et des câbles des portes coulissantes ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF6M","Porte coupe feu"," ","[...] Nettoyage des rails et glissières ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF6M","Porte coupe feu"," ","[...] Vérification de la liberté de fonctionnement des dispositifs de fermeture ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF6M","Porte coupe feu"," ","[...] Vérification de l'absence d'obstacle sur la porte ",1,5]
["SECO","Second Oeuvre","PCF","Porte coupe feu","PCF6M","Porte coupe feu"," ","[...] Inspection des systèmes de détection et vérification des sources d'alimentation",1,5]
["SECO","Second Oeuvre","POR","Porte"]
["SECO","Second Oeuvre","POR-BA","Porte battante"]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Contrôle du fonctionnement des poignées ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Contrôle de la serrure, du cylindre, de la gache ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Graissage des paumelles ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Contrôle du ferme porte ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Mise en jeu si besoin ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Contrôle de la butée au sol ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Vérification visuelle ",7,5]
["SECO","Second Oeuvre","SERR","Serrure","SERR1S","Serrures"," ","[...] Barre anti panique (porte coupe feu)",7,5]
["SECO","Second Oeuvre","STO","Store","STO1A","Store"," ","[...] Contrôle de la fixation  ",0.1,5]
["SECO","Second Oeuvre","STO","Store","STO1A","Store"," ","[...] Contrôle des guides ",0.1,5]
["SECO","Second Oeuvre","STO","Store","STO1A","Store"," ","[...] Contrôle des connexions électriques ",0.1,5]
["SECO","Second Oeuvre","STO","Store","STO1A","Store"," ","[...] Contrôle des lacettes ",0.1,5]
["SECO","Second Oeuvre","STO","Store","STO1A","Store"," ","[...] Contrôle du bon fonctionnement",0.1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","Opération réalisée par un prestataire: ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," "," ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","[...] Contrôle des étanchéités ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","[...] Déserbage, nettoyage et enlèvement des mousses ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","[...] Ratissage des gravillons (Si besoin) ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","[...] Contrôle des crépines des EP ",1,5]
["SECO","Second Oeuvre","TER","Entretien terrasse","TER1A","Entretien terrasse"," ","[...] Contrôle des avaloirs, des gouttières et des conduits de décharge",1,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL1A-HU","Colonne humide"," ","Colonnes: ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL1A-HU","Colonne humide"," ","[...] Contrôle de l'état du revêtement extérieur ( Contrôle réglementaire (opération sous- traitée) NF S 61-750) ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL1A-HU","Colonne humide"," ","[...] Essai de mise en eau (à prévoir et à exécuter en accord avec le centre de secours",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","Prises: ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","[...] Vérification de l'accessibilité aux prises et aux raccords ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","[...] Contrôle de la présence des bouchons de prise et de fermeture ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," "," ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","Colonnes: ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","[...] Vérification de l'absence de corps étrangers dans la colonne ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","[...] Vérification de la présence de la signalisation ",2,5]
["SINC","Sécurité Incendie","COL-HU","Colonne humide","COL3M-HU","Colonne humide"," ","[...] Vérification fonctionnelle",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL1A-SE","Colonne sèche"," ","Colonnes: ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL1A-SE","Colonne sèche"," ","[...] Contrôle de l'état du revêtement extérieur ( Contrôle réglementaire (opération sous- traitée) NF S 61-750) ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL1A-SE","Colonne sèche"," ","[...] Essai de mise en eau (à prévoir et à exécuter en accord avec le centre de secours",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","Prises: ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","[...] Vérification de l'accessibilité aux prises et aux raccords ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","[...] Contrôle de la présence des bouchons de prise et de fermeture ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," "," ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","Colonnes: ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","[...] Vérification de l'absence de corps étrangers dans la colonne ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","[...] Vérification de la présence de la signalisation ",2,5]
["SINC","Sécurité Incendie","COL-SE","Colonne sèche","COL3M-SE","Colonne sèche"," ","[...] Vérification fonctionnelle",2,5]
["SINC","Sécurité Incendie","CR","Coffret de relayge"]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA1A-CO","Extinction automatique CO2"," ","[...] Contrôle des EPI (masque respiratoire) suivant notice constructeur ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA1A-CO","Extinction automatique CO2"," ","[...] Tous les 10 ans: Révision de l'installation par installateur ou organisme qualifié APSAD ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA1A-CO","Extinction automatique CO2"," ","[...] Date de la dernière révision:……………..",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Contrôle de la charge ou de la pression des réservoirs ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Vérification fonctionnelle des vannes ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Vérification fonctionnelle sans émission : des commandes manuelles (bris de glace), des commandes automatiques (détecteurs)  ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Contrôle de l'état des flexibles, diffuseurs, canalisations ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Contrôle des signaux sonores et visuels (alarme 1 ton, 2 tons, panneaux lumineux) ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Contrôle du dispositif de retardement (temporisation < 1 minute) ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Vérification fonctionnelle du système d'arrêt automatique de la ventilation ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Vérification fonctionnelle du désenfumage ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Vérification fonctionnelle de la fermeture automatique des PCF, CCF, VCF ",2,5]
["SINC","Sécurité Incendie","EXA-CO","Extinction automatique CO2","EXA6M-CO","Extinction automatique CO2"," ","[...] Contrôle du fonctionnement des alarmes et de leur report",2,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT1A","Extincteur"," ","Opération réalisée par un prestataire: ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT1A","Extincteur"," "," ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT1A","Extincteur"," ","[...] Maintenance et contrôle par un technicien habilité  ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT1A","Extincteur"," ","[...] Enregistrement sur étiquette de vérification sur chaque appareil    ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT1A","Extincteur"," ","[...] Consignation de chaque contrôle dans le registre de sécurité",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","[...] Vérification de la présence et accessibilité des extincteurs à leur emplacement ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","[...] Vérification de leur état extérieur: ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","      - présence du plombage ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","      - présence de l'étiquette avec le nom du vérificateur ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","      - état du corps et de la lance ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","      - diffuseur non obstrué ",0.1,5]
["SINC","Sécurité Incendie","EXT","Extincteur","EXT3M","Extincteur"," ","      - dispositif de verrouillage intact",0.1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT1M","Poteaux et bouches d'incendie"," ","[...] Contrôle visuel de l'accessibilité et de l'état apparent, absence de fuites. ",0.25,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT1M","Poteaux et bouches d'incendie"," ","[...] Présence de la signalisation (bouches)",0.25,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Désengorgement de la vidange du coffre (bouches), ou de la colonne (poteaux). ",1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Vérification de l'état des bouchons, raccords, joints,&#133; ",1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Vérification de l'état de la soupape ",1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Vérification du fonctionnement du régulateur ",1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Graissage des tiges filetée du régulateur, charnière, genouillères, tourillons, &#133; ",1,5]
["SINC","Sécurité Incendie","POT","Poteaux et bouches d'incendie","POT6M","Poteaux et bouches d'incendie"," ","[...] Essais de fonctionnement comprenant le contrôle de la pression statique et du débit. (Inscription sur le registre de sécurité) (Opération réalisée par un prestataire)",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","Réseau d'alimentation: ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Vérifier pour le réseau d'alimentation ou de réalimentation des sources : ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - étanchéité  ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - fonctionnement des manomètres ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - pression de l'eau au manomètre situé en amont du R.I.A le plus défavorisé ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - vérifier le fonctionnement en eau à plein débit du RIA le plus défavorisé et d'un autre RIA (différent chaque trimestre) jusqu'à écoulement d'une eau claire ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","               ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","Pompes et surpresseurs: ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Vérifier le moteur d'entraînement des pompes :  ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - fonctionnement sans saccade du surpresseur ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - le dispositif de mise en route automatique doit fonctionner 3 fois consécutives sans défaillance avec un arrêt d'environ 1 minute entre chaque démarrage. ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","         ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","RIA: ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Vérifier l'état de tous les R.I.A par mise sous pression de service et contrôle d'aspect :  ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - du tuyau semi rigide en le déroulant complètement sur toute sa longueur ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - des fixations d'extrémité ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","      - des joints d'étanchéité ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Consignation du contrôle sur chaque RIA (Date et résultat de la vérification, signature de l'intervenant) ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Changer tous les joints d'étanchéité de chaque R.I.A et remplacer les tuyaux semi-rigides si nécessaire ",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1A","RIA"," ","[...] Contrôler l'état interne des tuyauteries par prélèvement pour analyse des manchettes prévues à cet effet",2,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Vérification de l'étanchéité et du fonctionnement des vannes de contre barrage, des RIA et tous les organes mécaniques de l'installation ",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Vérification de l'étanchéité et du fonctionnement de la source d'eau et contrôle du niveau d'eau ",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Vérification de l'état des dévidoirs (rotation, pivotement, choc éventuel) ",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Vérification de la présence de tous les éléments constitutifs des RIA (robinet diffuseur, ou autres accessoires) ",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Vérification de la mise en eau non sous pression des RIA (prêt à fonctionner) ",1,5]
["SINC","Sécurité Incendie","RIA","RIA","RIA1M","RIA"," ","[...] Relevé de la pression sur le manomètre du RIA le plus éloigné",1,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI3M","Système d'alarme incendie"," ","[...] Contrôle de l'aspect des déclencheurs manuels \" Bris de glace\" ",1,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI3M","Système d'alarme incendie"," ","[...] Contrôle de la charge de batterie des blocs autonomes d'alarme sonore",1,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Contrôle de la tension de la batterie ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Essai des signaux sonores et lumineux (Dérangement lignes, Alarme feu, mise hors service, défaut d'alimentation,&#133;..) ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Essai de l'ensemble des déclencheurs manuels \" bris de glace\" ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Contrôle du bon fonctionnement des blocs autonomes d'alarme sonore ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Contrôle des reports d'alarmes ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Essai des commandes manuelles de la baie de signalisation ",2,5]
["SINC","Sécurité Incendie","SAI","Système d'alarme incendie","SAI6M","Système d'alarme incendie"," ","[...] Remplacement des batteries des sources auxiliaires (Selon préconisation des constructeur)",2,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Contrôle de l'état des supports et des canalisations ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Contrôle du dispositif antigel ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Contrôle du dispositif anticorrosion ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Essai des performances initiales ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Rinçage des canalisations (tous les 1 à 6 ans selon la qualité de l'eau) ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," "," ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","Poste de contrôle sprinkler: ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Vérification du joint d'étanchéité, de l'ouverture totale du clapet ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Nettoyage du clapet d'alarme ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Nettoyage du filtre et de l'injecteur d'arrivée d'eau de la turbine du gong hydraulique et graissage des pièces en rotation  ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Contrôle du fonctionnement de l'accélérateur et des exhausteurs s'ils existent, selon les  préconisations des constructeurs ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Pour les installations sous air, contrôle du démarrage automatique du compresseur d'air par chute volontaire de la pression d'air ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," "," ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","Canalisation en amont du poste: ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Essai d'écoulement pour contrôle de la propreté de l'eau en bout de réseau ",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK1A","Extinction automatiq sprinkler"," ","[...] Contrôle de la protection cathodique des réseaux en acier",4,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK6M","Extinction automatiq sprinkler"," ","Poste de contrôle sprinkler: ",2,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK6M","Extinction automatiq sprinkler"," ","[...] Man&#156;uvre de la vanne d'arrêt du poste amont ",2,5]
["SINC","Sécurité Incendie","SPK","Extinction auto sprinkler","SPK6M","Extinction automatiq sprinkler"," ","[...] Pour les installations de type alternatif, procéder au passage sous eau ou sous air selon la saison",2,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI1M","Détection incendie"," ","[...] Contrôle de l'aspect des déclencheurs manuels (Bris de glace) ",1,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI1M","Détection incendie"," ","[...] Contrôle de la charge des batteries des blocs autonomes d'alarmes sonores",1,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","Opération réalisée par un prestataire: ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," "," ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","Baie: ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Relevé de la tension batterie ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Essai des signaux sonores et lumineux ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Essai de l'ensemble des bris de glace ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle du bon fonctionnement des diffuseurs sonores (BAAS) ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle des reports d'alarmes ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Essai des commandes manuelles du tableau de signalisation ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Remplacement des batteries auxiliaires (Tous les 4 ans ) Dernier remplacement : ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," "," ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","Détecteurs: ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Essai de 50% des détecteurs  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle de l'alarme sur la centrale  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification des indicateurs d'action  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle de la priorité d'alarme feu ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification des implantations des détecteurs en fonction des modifications ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," "," ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","Asservissements: ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification des scénarios avec essais réels et contrôle des asservissements (VCF, CCF, PCF, désenfumage)         ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," "," ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","Station d'énergie: ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification des tensions primaires et secondaires  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification et réglage du floating  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle de l'état des batteries  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Essais des batteries de secours  ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Vérification de la tension de décharge ",8,5]
["SINC","Sécurité Incendie","SSI","Système de sécurité incendie","SSI6M","Détection incendie"," ","[...] Contrôle de l'existence d'un stock de petite fourniture ",8,5]
["SINC","Sécurité Incendie","VT","Volet tunnel"]
["SPOR","Sport","PISC","Piscine"]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","Opération réalisée par un prestataire: ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," "," ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Vérification des protections de lignes ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle de la charge des batteries auxiliaires ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle des tensions ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle du serrage des connexions ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle des programmes horaires ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Essais des commandes et de la signalisation ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle des équipements de supervision ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle du bon fonctionnement des avertisseurs sonores ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle des détecteurs magnétiques (fenêtres, portes &#133;) ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Réglage de la sensibilité des détecteurs de présence et de l&#146;angle de détection ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Contrôle de la bonne transmission des alarmes (télé transmetteur, imprimante, modem, société de gardiennage&#133;)   ",4,5]
["STT","SOUS TRAITANT","ANI","Anti-intrusion","ANI1A","Anti-intrusion"," ","[...] Remplacement des batteries auxiliaires ( au moins tous les 4 ans )Date du dernier remplacement: &#133;&#133;&#133;&#133;&#133;&#133;&#133;&#133;&#133;&#133;",4,5]
["STT","SOUS TRAITANT","ASC","Ascenseurs et montes-charges","ASC1A","Ascenseurs et montes-charges"," ","Accompagnement du prestataire",1,5]
["STT","SOUS TRAITANT","ASC","Ascenseurs et montes-charges","ASC6M","Ascenseurs et montes-charges"," ","Accompagnement du prestataire",1,5]
["STT","SOUS TRAITANT","ASC","Ascenseurs et montes-charges","ASC6S","Ascenseurs et montes-charges"," ","Accompagnement du prestataire",0.5,5]
["STT","SOUS TRAITANT","CUI ENS","Ensemble matériel Cuisine","CUI6M","Matériel de cuisine"," ","[...] Maintenance des matériels de cuisine sous traitées",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","Opération réalisée par un prestataire: ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," "," ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Contrôle du fonctionnement  ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Vérification du bon déroulement du cycle ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Vérification des composants électriques ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Etalonnage de l'analyse à l'aide de gaz neutre et calibré ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Vérification des actions PV - GV et alarmes ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Nettoyage du filtre principal ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Nettoyage des filtres parking ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Controle d'étanchéité des lignes pneumatiques ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Vérification de la mise en alarme GV - PV de chaque niveau ",1,5]
["STT","SOUS TRAITANT","DCO","Détection CO","DCO1A","Détection CO"," ","[...] Réglage des débitmètre de gaz analysé",1,5]
["STT","SOUS TRAITANT","NAC","Nacelle de nettoyage","NAC6M","Nacelle de nettoyage"," ","Accompagnement du prestataire",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","Opération réalisée par un prestataire: ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," "," ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Vérification des éléments de guidage (rails, galets, roulements…) ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle des courroies ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Vérification des articulations (charnières, pivots…) ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Vérification des fixations et points d'encrage ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Vérification des systèmes d'équilibrage ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle des détecteurs de présence  ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle du fonctionnement à distance ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Réglage d'ouverture et fermeture ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle du verrouillage de la porte ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle de l'ouverture porte sur manque tension ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle de la signalisation sur porte transparente ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle moteur et vérification de l'état de fixation moteur ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle du bon fonctionnement des manœuvres de dépannage ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle des connexions électriques et resserrage ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Contrôle des sécurités électriques et mécaniques ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Nettoyage , graissage des axes , réglages et essais ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Remise d'un rapport à chaque fin de visite ",1,5]
["STT","SOUS TRAITANT","PAU-CO","Porte automatique coulissante","PAU6M-CO","Porte automatique coulissante"," ","[...] Renseignement du livret d'entretien porte et registre sécurité ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","Opération réalisée par un prestataire: ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," "," ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Vérification des éléments de guidage (rails, galets, roulements&#133;) ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle des courroies ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Vérification des articulations (charnières, pivots&#133;) ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Vérification des fixations et points d'encrage ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Vérification des systèmes d'équilibrage ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle des détecteurs de présence  ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle du fonctionnement à distance ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Réglage d'ouverture et fermeture ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle du verrouillage de la porte ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle de l'ouverture porte sur manque tension ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle de la signalisation sur porte transparente ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle moteur et vérification de l'état de fixation moteur ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle du bon fonctionnement des man&#156;uvres de dépannage ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle des connexions électriques et resserrage ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Contrôle des sécurités électriques et mécaniques ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Nettoyage , graissage des axes , réglages et essais ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Remise d'un rapport à chaque fin de visite ",1,5]
["STT","SOUS TRAITANT","PAU-TA","Porte automatique tambour","PAU6M-TA","Porte automatique tambour"," ","[...] Renseignement du livret d'entretien porte et registre sécurité ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC1M","Contrôle d'accès"," ","[...] Sauvegarde du programme",0.25,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","Opération réalisée par un prestataire: ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," "," ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","[...] Contrôle des réseaux de communication entre le superviseur et les lecteurs ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","[...] Analyse de l’historique et des événements survenus ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","[...] Purge des fichiers ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","[...] Sauvegarde système ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","CAC","Contrôle d'accès","CAC6M","Contrôle d'accès"," ","[...] Mise à jour logiciel",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","VSU","Vidéo-surveillance","VSU1A","Vidéo"," ","Opération réalisée par un prestataire : ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","VSU","Vidéo-surveillance","VSU1A","Vidéo"," "," ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","VSU","Vidéo-surveillance","VSU1A","Vidéo"," ","[...] Vérification du bon fonctionnement des enregistreurs vidéo ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","VSU","Vidéo-surveillance","VSU1A","Vidéo"," ","[...] Vérification du bon fonctionnement des caméras vidéo ",1,5]
["SUR","Sureté/Contrôle accès/Vidéo","VSU","Vidéo-surveillance","VSU1A","Vidéo"," ","[...] Vérification du bon fonctionnement des liaisons vidéo",1,5]