## Worksheet
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle | Nom Prénom | Signature du Technicien
MARTIN | Jean-Claude |  |  |  | 2017-06-07 11:42 | E1B17 | Industriel | Sous-sol | Éclairage et PC mise en fûts | Éclairage et PC mise en fûts |  | 2017-06-07 | OK | MAUVAIS | NOK | OK | NOK | OK | NOK | NOK |  | OK | [16 empty] | OK | 2017-06-07 | M. MARTIN Jean-Claude | c9404f210692su85671_20170607114153.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:54 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614185409.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:18 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614191725.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:49 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | voyant présence tension fusible2A HS | voyant présence tension led ref ZBV-M1 HS |  |  |  |  | remplacement des fusibles ok |  |  |  | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614192125.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-14 17:45 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614174433.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:37 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | voyant présence tension Hs réf 230v 20ma | [9 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614183726.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-15 15:51 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 |  | 2017-06-14 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | SANS OBJET | OK |  | OK | SANS OBJET | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170614203339.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:16 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER | F3A10.20 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616181553.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:24 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 | F3A15 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616182401.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:27 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 | F3A28.1 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616182627.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:29 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 | TRO2.1.8.12 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616182846.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:30 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 | TRO2.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616183008.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:50 | TRO2.1.8.13 | Industriel | Etage | LT SUD LIPANOR | GTC ZT LIPANOR | TRO2.1.8.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616184948.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:53 | F6A2 | Industriel | Etage | ZT SUD | Atelier DEPAKINE GLATT4 | F6A2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | SANS OBJET | OK | OK | OK | OK | OK | [10 empty] | NOK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616185322.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:58 | F6A2.2 | Industriel | Etage | ZT Sud | CTA GLATT 4 | F6A2.2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK |  | OK | NOK | OK | OK | OK | OK | OK | filtre de la ventilation son sale | [8 empty] | remplacement des filtre ok | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616185805.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:02 | F3A15.1 | Industriel | Etage | ZT SUD LIPANOR | PMA800 FIELDER 7 PUISSANCE | F3A15.1 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616190210.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:17 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 | TRO2.1.8.17 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616191658.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:57 | F3A20.13.11 | Industriel | Etage | LT SUD LIPANOR | CTA LIPANOR | F3A20.13.11 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616195642.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:02 | F3D2 | Industriel | Etage | ZT Sud | Puissance Granulateur Fielder Laf 2 | F3D2 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-16 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616200131.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:08 | TRO2.1.8.5 | Industriel | Etage | ZT Sud | Automatisme FIELDER. LAF2 granulateur | TRO2.1.8.5 | 2016-06-16 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16 | M. PELTIER Jean-Marc | c9404f210692su85671_20170616200734.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:26 | F3A20.12 | Industriel | Etage | ZT SUD | CA 1019 | F3A20.12 | 2016-08-15 | OK | MOYEN | NOK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630182537.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:35 | F3A11 | Industriel | Etage | ZT SUD | CA 1006 CLIM TRANXENE | F3A11 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630183434.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:43 | F3D9.5 | Industriel | Etage | ZT SUD | CTA LAF 5 | F3D9.5 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630184234.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:52 | TRO2.1.16 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD GTC | TRO2.1.16 | 2016-08-18 | OK | BON | OK | OK | SO | OK | OK | NOK | NOK | OK | SO | OK | NOK | OK | OK | OK | plastron enlevé suite a la thermographie mais remis en place | [8 empty] | remise en place des plastrons | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630185215.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 19:13 | TRO2.1 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD PLATEAU INDUS | TRO2.1 | 2016-08-26 | OK | BON | OK | OK | SO | OK | OK | OK | NOK | OK | SO | OK | NOK | OK | OK | OK | plan a remettre à jour | manque obturateurs | [8 empty] | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630191320.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:28 | F3A10 | Industriel | Etage | ZT SUD | Distribution divers | F3A10 | 2016-08-26 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | prevoir nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630202800.jpg
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:31 | F3D9 | Industriel | Etage | ZT SUD | Distribution divers | F3D9 | 2016-08-23 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir le nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30 | M. PELTIER Jean-Marc | c9404f210692su85671_20170630203044.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:25 | F3A10.2 | Industriel | Etage | ZT SUD | PC + divers LAF 5 | F3A10.2 | 2016-08-12 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | disjoncteur tombée F3A10.2.7 pc atelier 5 | [9 empty] | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712191613.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.2.2 | Industriel | Etage | ZT SUD | CMA LAF 5 | F3A10.2.2 | 2016-08-12 | OK | BON | OK | OK | OK |  | OK | OK | OK |  | SO | OK | NOK | OK | OK | OK | manque cache goulotte | [8 empty] | mise en place d'un cache goulotte | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712193028.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.21 | Industriel | Etage | ZT SUD | CMA LAF 1 | F3A10.21 | 2016-08-12 | OK | OBSOLETE | NOK | OK | SO | SO | SO | SO | SO | SO | SO | OK | SO | OK | OK | OK | armoire consigné mise l'arrêt complet | [9 empty] | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712193608.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A20.8.1 | Industriel | Etage | ZT SUD | Retournement + variateur LAF 1 | F3A20.8.1 | 2016-08-12 | OK | OBSOLETE | NOK |  | SO | OK | OK | OK | OK | SO | SO | OK | SO | OK | OK | OK | général armoire disjonter | [9 empty] | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712194216.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.2.1 | Industriel | Etage | ZT SUD | Variateur pompes LAF 5 | F3A10.2.1 | 2016-08-12 | OK | MOYEN | OK | OK | OK | NOK | OK | NOK | NOK | OK | NOK | OK | OK | OK | OK | OK | armoire très sale | manque plan | prévoir le remplacement du filtre | [6 empty] | nettoyage de l'armoire | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712195924.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | TRO2.1.15 | Industriel | Etage | ZT SUD | FIELDER 5 SECOURU automate | TRO2.1.15 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | NOK | OK | OK | OK | grille de ventilation cassé prévoir a la remplacer | manque cache goulotte | [8 empty] | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712201214.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.3 | Industriel | Etage | ZT SUD | FIELDERS 5 PUISSANCE | F3A10.3 | 2016-08-12 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prevoir le remplacement des filtres | prévoir le nettoyage de l'armoire | [7 empty] | remplacement des filtres de ventilation et nettoyage de l'armoire | OK | 2017-07-12 | M. PELTIER Jean-Marc | c9404f210692su85671_20170712203334.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:37 | TRO2.1.5 | Industriel | Etage | ZT SUD | LAF 5 SECOURU automate | TRO2.1.5 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir nettoyage de l'armoire | [8 empty] | nettoyage de l'armoire le 13/07/2017 | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713182527.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:37 | F3A10.8 | Industriel | Etage | ZT SUD | AUTOMATE LAF5 | F3A10.8 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir nettoyage de l'armoire | [8 empty] | nettoyage de l'armoire le 13/07/2017 | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713190501.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3A17 | Industriel | Etage | ZT SUD | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-08-13 | OK | BON | OK | OK | SO | NOK | OK | NOK | NOK | OK | SO | OK | NOK |  | SO | OK | prévoir nettoyage de l'armoire | manque plan | manque obturateur | [6 empty] | nettoyage de l'armoire ,remise en place des obturateurs | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713190858.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3A20.8 | Industriel | Etage | ZT SUD | EXTRACTION/VENTILATION LAF 1 | F3A20.8 | 2016-08-13 | OK | MOYEN | NOK | OK | SO | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | général de l'armoire est a l'arrêt | [9 empty] | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713191905.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3D9.1 | Industriel | Etage | ZT SUD | FIELDER LAF 3 | F3D9.1 | 2016-08-13 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713193034.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3D9.1.2 | Industriel | Etage | ZT SUD | CMA LAF 3 | F3D9.1.2 | 2016-08-13 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | [10 empty] | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713194013.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | TRO2.1.3 | Industriel | Etage | ZT SUD | LAF 3 AUTOMATE | TRO2.1.3 | 2016-08-13 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage des filtres de ventilation | [8 empty] | nettoyage des filtres de la ventilation | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713195720.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:51 | F3A20.11.1 | Industriel | Etage | ZT SUD | LAF 3 AUTOMATE | F3A20.11.1 | 2016-08-13 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir remplacement voyant ref ZBV-M1 230v | prévoir le nettoyage des filtres de la ventilation | [7 empty] | nettoyage des filtres de la ventilation | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713200141.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:51 | F3D9.1.1 | Industriel | ETAGE | ZT SUD | Variateur FIELDER LAF 3 | F3D9.1.1 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage de l'armoire | prévoir le remplacement des filtres ventilation | [7 empty] | nettoyage de l'armoire,remplacement des filtres de la ventilation | OK | 2017-07-13 | M. PELTIER Jean-Marc | c9404f210692su85671_20170713202657.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:29 | F1A17 | Industriel | Etage | ALIM ZONE | ALIM ZONE | F1A17 | 2016-08-17 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717203111.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:30 | TRO3.2.10 | Industriel | Etage | RECEPTION MP | GTC etage nord | TRO3.2.10 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717203741.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:31 | F1A17.13 | Industriel | Etage | RECEPTION | WESPACKS reception MP | F1A17.13 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717204444.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:31 | F1A17.17 | Industriel | Etage | RECEPTION MP | PA2082 | F1A17.17 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717204803.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:32 | F1B10.6 | Industriel | Etage | RECEPTION MP | aerothermes quai reception | F1B10.6 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717205903.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:33 | TRO3.2.5 | Industriel | Etage |  | Arrosage Sprinkler exterieur portakabin | TRO3.2.5 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717210237.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:34 | F1A24.2 | Industriel | Etage | Quai nord | PA PORTES NOMAFA ETAGE RECEPTION | F1A24.2 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717211204.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:34 | F1A24.2.1 | Industriel | Etage | RECEPTION MP | PA1054 PA1053 | F1A24.2.1 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717211446.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:35 | F1A17.21 | Industriel | Etage | QUAI NORD | PC eclairage chargeurs rideaux | F1A17/21 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717212427.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:35 | F1A17.21.21 | Industriel | Etage | CONVOYEUR RECEPTION | CONVOYEUR RECEPTION | F1A17.21.21 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17 | M. LEROY Emmanuel | c9404f210692su85671_20170717212855.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:34 | F1B22 | industriel | Etage | Travée B matières premières | CA 1067 | F1B22 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | disjoncteur thermique Q13 consigne | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720183625.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:35 | F1A17.5 | Industriel | Etage | Box prelevement 2 | Box prelevement 2 | F1A17.5 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720184231.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:38 | F1A17.26 | Industriel | Etage |  | Coffret banderoleuse | F1A17.26 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720184856.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:38 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720185921.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:44 | ?1 | Industriel | Sous-sol nord | Clim poste 1 | Coffret détection feu | ? | 2016-08-20 | OK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | OK | pas numero d'armoire | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720190609.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:48 | F1A17.12 | Industriel | Etage | CENTRALE PRELEVEMENT | CENTRALE PRELEVEMENT | F1A17.12 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720190812.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:57 | F1A17.21.2.11 | Industriel | Etage |  | porte 7 quai nord | F1A17.21.2.11 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720202400.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:58 | F1A17.21.2.3 | Industriel | Etage |  | PA2106 (porte n°7) | F1A17.21.2.3 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720202723.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:59 | F1A17.9.6.4 | Industriel | Etage |  | Pont hydraulique (porte n°6) | F1A17.9.6.4 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720202953.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:00 | F1A17.21.22 | Industriel | Etage |  | rideau rapide nergeco | F1A17.21.22 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720203236.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:00 | F1A17.21.2.4 | Industriel | Etage |  | PA2105 (porte n°6) | F1A17.21.2.4 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720203532.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:01 | ?2 | Industriel | etage | quai nord | coffret gestion interverrouillage porte quai | ? | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720203838.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:02 | F1A17.21.2.11 | Industriel | Etage |  | rideau rapide nergeco | F1A17.21.2.11 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720204053.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:03 | F1A17.21.2.10 | Industriel | Etage | QUAI NORD | Coffret gestion SAS magasin | F1A17.21.2.10 | 2016-08-20 | OK | BON | SO | OK | OK | OK |  | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720204312.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:03 | F1A17.21.2 | Industriel | Etage | QUAI NORD | Armoire rideaux | F1A17.21.2 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720204533.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:04 | F1A17.21.22 | Industriel | Etage |  | table elevatrice | F1A17.21.22 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720204925.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:04 | F1A17.18 | Industriel | Etage | quai nord | coffret electro aimant | F1A17.18 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720205143.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:05 | F1A17.21.2.5 | Industriel | Etage | quai nord | PA2104 (porte n°5) | F1A17.21.2.5 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720205419.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:06 | F1A17.9.6.6 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.6 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720205610.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:06 | F1A17.21.2.6 | Industriel | Etage | quai nord | PA2103 (porte n°4) | F1A17.21.2.6 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720205838.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:07 | F1A17.21.2.7 | Industriel | Etage |  | Pont Hydraulique PA2102 (porte n°3) | F1A17.21.2.7 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720210324.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:07 | F1A17.21.2.7 | Industriel | Etage | quai nord | Pont Hydraulique PA2102 (porte n°3) | F1A17.21.2.7 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720210507.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:08 | F1A17.9.6.8 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.8 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720210706.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:08 | F1A17.21.2.8 | Industriel | Etage | quai nord | PA2101 | F1A17.21.2.8 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720210856.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:09 | ?3 | Industriel | etage | quai nord | PA1202 | ? | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | NOK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720213412.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:09 | F1A17.9.6.9 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.9 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720211251.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:10 | E1B5.12 | Industriel | Etage | RECEPTION G25 | quai nord | E1B5.12 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20 | M. LEROY Emmanuel | c9404f210692su85671_20170720211613.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:54 | F3A10.15 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR PMA 800 | F3A10.15 | 2016-07-25 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK |  | OK | OK | prevoire le remplacement des filtres | prevoire le remplacement de l'éclairage de l'armoire ref 2*7w cft/827 2b | [8 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725221132.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:54 | TRO2.1.8.2 | Industriel | Etage | LT SUD LIPANOR | MELANGEUR AUTOMATE FIELDER4 | TRO2.1.8.2 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725215347.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:55 | F3A28.2 | Industriel | Etage | LT SUD LIPANOR | ARMOIRE PUISSANCE LAF 4 | F3A28.2 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation Hs prevoire remplacement ventilateur | [9 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725215014.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:55 | F3A28.3 | Industriel | Etage | ZT Sud | atelier laf 4 calibreur CMA / PEROLO LAF 4 | F3A28.3 | 2016-07-25 | OK | BON | OK | OK | NOK | OK | OK | NOK | NOK |  | OK | OK | OK | OK | OK | OK | voyant marche calibreur hs ref 24v 125ma | manque plan | [7 empty] | remplacent du voyant 24v le 25/07/2017 | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725213032.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:00 | F3A28 | Industriel | Etage | ZT Sud | FIELDER LAF 4 | F3A28 | 2016-07-25 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | voyant hs et fusible | manque obturateur | [8 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725211522.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:01 | TRO2.1.8 | Industriel | Etage | ZT SUD LIPANOR | COFFRET ETAGE ZT SUD | TRO2.1.8 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | NOK | OK | SO | OK | OK | OK | OK | OK | mettre a jours le plan | [9 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725210034.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:02 | F3A20.6 | Industriel | Etage | LT SUD LIPANOR | Éclairage + PC LIPANOR | F3A20.6 | 2016-07-25 | OK | BON | NOK | OK | OK | OK | NOK | OK | OK | OK | SO | OK | OK | OK | OK | OK | disjoncteur couper D12,D14,D15,D16 | sortie de cable reste des cables couper dans chemin de cable et brancher au bornier | [8 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc | c9404f210692su85671_20170725204843.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:03 | F3A15.1 | Industriel | Etage | ZT SUD LIPANOR | PMA800 FIELDER 7 PUISSANCE | F3A15.1 | 2016-07-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-25 | M. PELTIER Jean-Marc
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A21.7.16 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR WP170 RDC SAS PS | F3A21.7.16 | 2016-07-26 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | porte document arracher prévoir de le remettre | [8 empty] | remise en place du porte document le 26/07/2017 | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726200534.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A20.13.26 | Industriel | Etage | LT SUD LIPANOR | COFFRET SAS PERSONNEL IMA 6 LIPANOR | F3A20.13.26 | 2016-07-26 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | SO | OK | OK | OK | SO | OK | [10 empty] | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726201134.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 | F3A28.1 | 2016-07-26 | OK | MAUVAIS | OK | OK | SO | NOK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | armoire très sale prévoir le nettoyage | [8 empty] | nettoyage e l'armoire le 26/7/2017 | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170727194409.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A20.9 | Industriel | Etage | ZT SUD | puissance LAF2 | F3A20.9 | 2016-07-26 | OK | MOYEN | OK | OK | NOK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | voyant retourneur en service hs 24v | moteur ventilation ne fonctionne plus prevoire le remplacement | prevoire le nettoyage de l'armoire | [6 empty] | nettoyage de l'armoire et remplacement du voyant le2 6/07/2017 | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726213114.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | TRO2.1.2 | Industriel | Etage | Local technique LAF 2 / 4 | Automatisme LAF 2 | TRO2.1.2 | 2016-07-26 | OK | MOYEN | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage de l'armoire | prévoir le remplacement des 2 moteur de ventilation | [7 empty] | nettoyage de l'armoire le 26/07/2017 | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726213431.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | Industriel | Etage | ZT SUD | Retourneur laf 2 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | 2016-07-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726214852.jpg
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | Industriel | Etage | ZT SUD | Retourneur laf 2 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | 2016-07-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-26 | M. PELTIER Jean-Marc | c9404f210692su85671_20170726214852.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:42 | F3A20.11 | Industriel | Etage | ZT SUD | Retourneur et ventillateur LAF 3 | F3A20.11 | 2016-08-21 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK |  | OK | OK | prevoire le nettoyage du filtre de la ventilation | [9 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821194150.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:47 | F3D9.6 | Industriel | Etage | Technique Sud | LAF 5 +TRANXENE SECOURS RESEAU EAU GLYCOLEE | F3D9.6 | 2016-08-21 | OK | BON | NOK | OK | SO | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | disjoncteur général à l'arrêt | [9 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821194635.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:52 | F3A20 | Industriel | Etage | ZT SUD | Distribution divers | F3A20 | 2016-08-21 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821195159.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:11 | F3A20.4 | Industriel | Etage | ZT SUD | ATELIER LAF 3 CUVES MAXILASE/VICTU | F3A20.4 | 2016-08-21 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821201052.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:26 | F3D3.2 | Industriel | Etage | ZT Sud Ouest | CTA LAF 1 | F3D3.2 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK |  | OK | OK | OK | prévoir remplacement des filtres ventilation | [9 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821202546.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:40 | F3D3.3 | Industriel | Etage | ZT Sud Ouest | CA1120 DCE LAF 3 | F3D3.3 | 2016-08-21 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | disjoncteur Q12 disjoncté alim voyant | voyant non alimenter | [7 empty] | voir avec cofely pour alim voyant | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821203944.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:56 | F3D3.1 | Industriel | Etage | ZT Sud Ouest | CTA LAF 2 | F3D3.1 | 2016-08-21 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | les voyants de signalisation de fonnctionnement et de de faut ne fonctionne pas cause la fixation du contacte est hs ref ZBE-205 telemecanique a remplacer | [9 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821205625.jpg
MARTIN | Jean-Claude |  |  |  | 2017-08-21 21:03 | F3D3.5 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT AIR box pesee 6 | F3D3.5 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir remplacement filtre ventilation | [9 empty] | OK | 2017-08-21 | M. PELTIER Jean-Marc | c9404f210692su85671_20170821210253.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-12 13:51 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2017-09-12 | OK | BON | [24 empty] | OK | 2017-09-12 | M. MARTIN Jean-Claude | c9404f210692su85671_20170912135026.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-12 13:58 | F3D3.3.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEREUR laf 3 | F3D3.3.3 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-12 | M. MARTIN Jean-Claude | c9404f210692su85671_20170912135807.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-13 08:02 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-12 | M. MARTIN Jean-Claude | c9404f210692su85671_20170913080127.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-13 08:36 | F3D3.2.3 | Industriel | Etage | ZT Sud | DCE LAF 1 | F3D3.2.3 | 2017-09-12 | OK | BON | NOK | OK | OK | OK | OK | OK | OK |  | SO | OK | OK | OK | OK | OK | Inter general de l'armoire est consigné depuis 05/07/2017 | Fils débranché dans l'armoire | [8 empty] | OK | 2017-09-12 | M. MARTIN Jean-Claude | c9404f210692su85671_20170913083611.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:01 | F3D3.4.3 | Industriel | Etage | ZT Sud Ouest | DCE LAF 5 | F3D3.4.3 | 2017-09-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | SO | SO | OK | OK | OK | OK | OK | remettre les schémas dans l'armoire | [9 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170914112939.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:03 | F3D3.7 | Industriel | Etage | ZT Sud Ouest | DCE GRANULATEUR CONTINU ud1100 | F3D3.7 | 2016-08-14 | OK | BON |  | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170914114130.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:04 | F3D3.4 | Industriel | Etage | ZT Sud Ouest | CTA LAF5 | F3D3.4 | 2016-08-14 | OK | BON |  | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | Il faut re fixer le porte plans | [9 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170914115156.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:07 | F3D3.6 | Industriel | Etage | ZT Sud Ouest | DCE CALIBRAGE 2 BOX 2 | F3D3.6 | 2016-08-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170915120624.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:10 | F3D4 | Industriel | Etage | ZT SUD OUEST | Distribution divers GLATT 2 | F3D4 | 2016-08-14 | OK | BON | OK |  | OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170915120859.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:12 | F3D5 | Industriel | Etage | ZT SUD OUEST | Glatt 6 | F3D5 | 2016-08-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | [10 empty] | OK | 2017-09-14 | M. MARTIN Jean-Claude | c9404f210692su85671_20170915121126.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:17 | F3A10.9 | Industriel | Etage | Zone technique LAF 1, 3, 5 TRAVEE D | ECL SALLE LAVAGE | F3A10.9 | 2016-08-18 | OK | BON | OK | OK | SO | OK | OK | NOK | SO | SO |  | OK | OK | OK | OK | OK | Remettre le plans dans le coffret | [9 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918221709.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:20 | F3D3 | Industriel | Etage | ZT OUEST | Éclairage zone technique sud-ouest | F3D3 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | Mettre le schema a jour | [9 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918222008.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:24 | F3D3.9 | Industriel | Etage | ZT OUEST | Distribution divers | F3D3.9 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | [10 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918222401.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:27 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 2 | F3D4.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918222648.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:30 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | ATELIER GLATT 2 MAXILASSE PELLICULAGE | F3D4.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918222953.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:34 | F3D5.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 6 | F3D5.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918223419.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:42 | F3D10.6 | Industriel | Etage | ZT Sud | DCE box 5 UD1089 | F3D10.6 | 2016-08-18 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170918224117.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 16:20 | F3D5.2 | Industriel | Etage | ZT SUD | Distribution divers GLATT 6 | F3D5.2 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | [16 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919162008.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 16:21 | TRO2.3.21.2 | Industriel | Etage | ZT OUEST | automate Glatt 6 | TRO2.3.21.2 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | [17 empty] | OK | 2017-09-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919162112.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 21:59 | F3D3.9.9 | Industriel | Etage | ZT Sud Ouest | Alim coffret gestion DCE | F3D3.9.9 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919215847.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:04 | TRO2.1.16 | Industriel | Etage | ZT SUD OUEST | ZT Ouest phase 1 GTC | TRO2.1.16 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | NOK |  | OK | OK | OK | OK | OK | OK | OK | mettre les schémas dans l'armoire | [9 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:07 | F3D9.3 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT D'AIR DEPAKINE BOX 6 | F3D9.3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919220701.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:11 | F3A10.17.21 | Industriel | Etage | ZT SUD OUEST | SAS Rideau/Porte BOX PESEE | F3A10.17.21 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919221044.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:17 | E3A3 | Industriel | Etage | Éclairage box de pesées | Éclairage box de pesées | E3A3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | Mise à jour les plans | [9 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919221701.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:20 | F3A10.17 | Industriel | Etage | ZT OUEST | PC BOX PESEE | F3A10.17 | 2016-08-19 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919221944.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:24 | TRO2.1.11 | Industriel | Etage | ZT Sud | DISTRIBUTION EAU PURIFIEE YOKOGAWA PROCESS | TRO2.1.11 | 2016-08-19 | OK | BON |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919222355.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:26 | TRO2.2 | Industriel | ETAGE | ZT OUEST | SALLE INFOR. BOX PESEE | TRO2.2 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919222612.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:30 | F3A10.17.25 | Industriel | Etage | ZT Sud | Boucle d'eau purifiée | F3A10.17.25 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919222934.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:33 | F3D3.13 | Industriel | ETAGE | ZONE TECHNIQUE SUD | TRAITEMENT AIR GRANULATION CONTINU | F3D3.13 | 2016-08-19 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919223213.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:35 | F3A10.17.29 | Industriel | Etage | ZT OUEST | CENTRALE DE PESAGE BOX 2 | F3A10.17.29 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919223446.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:37 | F3A10.17.28 | Industriel | Etage | ZT OUEST | CENTRALE DE PESEE BOX 5,PROCESS | F3A10.17.28 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170919223645.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 17:19 | F3A10 | Industriel | Etage | ZT SUD | Distribution divers | F3A10 | 2016-08-20 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | D10 consigné depuis le 29/08/2016 | [8 empty] | voir si le depart 18 n'est plus utilisé de supprimer le cadenas est le mettre en Resrve | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920171830.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 17:26 | F3D10.3 | Industriel | Etage | ZT ouest | CTA labo prod | F3D10.3 | 2016-08-20 | OK | BON | NOK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | Armoire cosigné depuis le 30/07/2015 par cofely | CTA en cours de démontage | [8 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920172535.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:32 | F3D4.2 | Industriel | Etage | ZT Sud OUEST | Puissance GLATT 2 | F3D4.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920203218.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:35 | TRO2.3.20.2 | Industriel | Etage | ZT SUD OUEST | PROCESS AUTOMATE GLATT 2 | TRO2.3.20.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920203438.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:39 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 2 | F3D4.1 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920203851.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:41 | F3D10.23 | Industriel | Etage | ZT Sud-Ouest | CTA BOX DE PESEE 2 | F3D10.23 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204028.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:42 | F3D10.25 | Industriel | Etage | ZT Sud-Ouest | DEPOUSSIERREUR BOX PESEE 1-2-3-4-5 | F3D10.25 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204225.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:44 | F3D9.3 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT D'AIR DEPAKINE BOX 6 | F3D9.3 | 2016-08-20 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204409.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:46 | F3D10.16 | Industriel | Etage | ZT SUD | TRAITEMENT D'AIR LOCAUX POICONS | F3D10.16 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204556.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:48 | F3D5.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 6 | F3D5.1 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204734.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:49 | F3D10.5 | Industriel | Etage | ZT Sud-Ouest | CTA BOX 5 | F3D10.5 | 2016-08-20 | OK | MAUVAIS | [14 empty] | A ncienne arrmoire consigné depuis 15/08/ 2015 | En cours de demontage | [8 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920204921.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:51 | F3D10.24 | Industriel | Etage | ZT ouest | CTA BOX DE PESEE 1-3-4 | F3D10.24 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920205056.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:56 | F3D10.5 | Industriel | Etage | ZT Sud-Ouest | CTA BOX 5 | F3D10.5 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Nouvelle Armoire box pesée No 5 | [9 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920205550.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:58 | F3D10.2 | Industriel | Etage | ZT Sud-Ouest | TRAITEMENT AIR CELLULES COMPRESSIONS 9,10,11 | F3D10.2 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920205735.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:59 | F3D10.22 | Industriel | Etage | ZT Sud-Ouest | UD1071 (DCE GELLULEUSE) | F3D10.22 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920205921.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:01 | F3D10.17 | Industriel | Etage | ZT SUD OUEST | DEPOUSSIREUR Accela cota | F3D10.17 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920210048.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:03 | TRO2.1.16 | Industriel | Etage | ZT SUD OUEST | ZT Ouest phase 1 GTC | TRO2.1.16 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920210227.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:04 | TRO2.3.20.2 | Industriel | Etage | ZT SUD OUEST | PROCESS AUTOMATE GLATT 2 | TRO2.3.20.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920210406.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:08 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920210729.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:35 | F3D4.2 | Industriel | Etage | ZT Sud OUEST | Puissance GLATT 2 | F3D4.2 | 2016-09-20 | OK | BON | OK | [23 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920223511.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:37 | F3F9.2 | Industriel | Etage | ZT ouest | PUISSANCE GLATT 5 | F3F9.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920223655.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:38 | F3F9 | Industriel | Etage | ZT ouest | ALIM GENERALE GLATT 5 | F3F9 | 2016-09-20 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920223821.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:40 | F3F9.1 | Industriel | Etage | ZT ouest | CTA GLATT 5 | F3F9.1 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920224000.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:42 | F8A16.3 | Industriel | Etage | ZT OUEST | TRAITEMENT AIR GLATT 7 | F8A16.3 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20170920224140.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:20 | F3D10.7 | Industriel | Etage | ZT ouest | Coffret Depoussiereur UD1070 | F3D10.7 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921171958.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:21 | TRO3.7.13.3 | Industriel | Etage | ZT Ouest | Automatisme GLATT 5 | TRO3.7.13.3 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921155112.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:53 | F3A32 | Industriel | Etage | ZT OUEST | Chambre froide, chambre deshy PC | F3A32 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921175311.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:09 | F8A15 | Industriel | Etage | ZT OUEST | PUISSANCE GLATT 7 | F8A15 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921180846.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:11 | TRO3.7.17 | Industriel | Etage | ZT Ouest | AUTOMATE GLATT 7 PROCESS | TRO3.7.17 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921181042.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:16 | F3A32.1 | Industriel | Etage | ZT ouest | CTA CHAMBRE DESHYDRATEE | F3A32.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921181547.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 20:44 | F3A10.10 | Industriel | Etage | MAINTENANCE MULTI PRODUIT | ATELIER REGLEURS MAINTENANCE | F3A10.10 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921204403.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:02 | F3A10.4 | Industriel | Etage | BUREAU Opérateur Laveuse | STATION DE LAVAGE CONTAINERS | F3A10.4 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921210145.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:07 | TRO2.1.9 | Industriel | Etage | BUREAU Opérateur Laveuse | STATION DE LAVAGE CONTAINERS SECOURUE | TRO2.1.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921210644.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:19 | F3A10.17.21.2 | Industriel | Etage |  | PA1155 | F3A10.17.21.2 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921211850.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:09 | F3A10.17.21.9 | Industriel | Etage |  | PA1151 | F3A10.17.21.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921220834.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:32 | F3A10.17.21.1 | Industriel | Etage |  | PA1162 | F3A10.17.21.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921223128.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:33 | F3A10.17.21.1 | Industriel | Etage |  | PA1162 | F3A10.17.21.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921223259.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:34 | F3A10.17.21.3 | Industriel | Etage |  | PA1153 | F3A10.17.21.3 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921223416.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:36 | F3A10.17.21.7 | Industriel | Etage |  | PA1159 | F3A10.17.21.7 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921223532.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:39 | F2A8.9 | Industriel | Etage |  | PA1140 | F2A8.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921223925.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:43 | F3A10.19 | Industriel | Etage |  | FLUX LAMINAIRE BOX N° 4 | F3A10.19 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921224206.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:45 | F3D9.4 | Industriel | Etage | face mireuse EISAI 2 | ATELIER BOX 6 DEPAKINE | F3D9.4 | 2017-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921224438.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:51 | F2A8.1.9 | Industriel | Etage | COULOIR DEPAKINE SUD | PA1307 | F2A8.1.9 | 2017-09-21 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21 | M. MARTIN Jean-Claude | c9404f210692su85671_20170921225055.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 16:40 | PA1129 | Industriel | Etage | STOCKAGE CONTENEUR | PA1129 | PA1129 | 2016-10-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | Pas de repere de provenance d'alimentation | [9 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922163754.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 16:44 | F3A20.13.24 | Industriel | Etage | STOCKAGE PROVISOIRE LIPANOR | Coffret PA1114 | F3A20.13.24 | 2016-07-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922164405.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:03 | TRO3.1 | Industriel | Etage | magasin | ARM. DISTRIBUTION P.C. BUREAUX | TRO3.1 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | Mettre les plans dans l'armoire | [9 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922180246.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:12 | F2A8 | Industriel | Etage | Magasin | ARM. DISTRIBUTION COURANT FORT | F2A8 | 2016-09-22 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | voyant h.s. | 2eme porte n'est pas relié à la terre | [7 empty] | Changé le voyant par 1 ZBV-M1 et relié la porte de gauche à la terre | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922181221.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:21 | E2A3 | Industriel | Etage | ZT OUEST | Éclairage liquide | E2A3 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | La porte de gauche n'est pas relié à la terre | Des fils non raccordé a mettre dans wagos | [7 empty] | Mettre la porte gauche à la terre et isolé les fils non raccordé | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922182051.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:28 | F2A8.1.15 | Industriel | Etage | NERI | PA1104 | F2A8.1.15 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922182811.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:39 | F2A8.1.16 | Industriel | Etage | EISAI 2 | PA1252 | F2A8.1.16 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922183915.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 19:03 | TRA1.3.4 | Industriel | Etage | couloir injectable etage | clim salle info ?? | TRA1.3.4 | 2017-09-22 | NOK | MOYEN | OK | OK | OK | OK | OK | NOK | NOK | [7 empty] | ARMOIRE HORS TENSION | [9 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922190302.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:16 | F3A20.13.5 | Industriel | Etage | MISE EN GELLULE | GELLULEUSE LIPANOR | F3A20.13.5 | 2017-09-22 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | juste un boîtier de coupure a proximité | [9 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922201538.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:24 | F3A10.15 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR PMA 800 | F3A10.15 | 2017-09-22 | NOK | OBSOLETE | [14 empty] | ARMOIRE NON TROUVÉ PROBABLEMENT SUPPRIMER | [9 empty] | NOK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922202302.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:26 | F3A19 | Industriel | Rdc | TRAVEE D | Machinerie mc2 | F3A19 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922202510.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:30 | TRO2.4.6 | Industriel | etage | bureaux injectable etage locl fournitures |  | TRO2.4.6 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922203009.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:33 | TRO2.4.6 | Industriel | etage | bureaux injectable etage locl fournitures |  | TRO2.4.6 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922203147.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:37 | F2A8BIS.9 | Industriel | Etage | Couloir centrale porte magasin | PA1260 | F2A8BIS.9 | 2017-09-22 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922203714.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:40 | F2A8BIS9 | Industriel | Etage | Couloir central Porte magasin | PA1225 | F2A8BIS9 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | [17 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922204028.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:43 | TRO3.1.9 | Industriel | Etage | COTE MC4 | ZT INJECTABLE GTC | TRO3.1.9 | 2016-09-22 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922204242.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:45 | F2A5 | Industriel | Etage | Couloire près MC 4 | CTA mirage | F2A5 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922204454.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:47 | F3A17 | Industriel | Etage | ZT SUD couloir | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922204707.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:50 | F2A8.1.9 | Industriel | Etage | COULOIR DEPAKINE SUD | PA1306 | F2A8.1.9 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922204943.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:55 | F2A8.1.7 | Industriel | Etage | EISAI3 MIREUSE | PA1197 | F2A8.1.7 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Le même départ alimente la porte 1198 | [9 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20170922205455.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:27 | TRO3.24 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.24 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26 | M. MARTIN Jean-Claude | c9404f210692su85671_20170926112701.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:31 | TRO3.3 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.3 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26 | M. MARTIN Jean-Claude | c9404f210692su85671_20170926113108.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:34 | E4A9 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A9 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26 | M. MARTIN Jean-Claude | c9404f210692su85671_20170926113423.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:27 | TRO3.24 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.24 | 2016-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. MARTIN Jean-Claude | c9404f210692su85671_20170927082702.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:38 | E4A13 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A13 | 2016-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. MARTIN Jean-Claude | c9404f210692su85671_20170927083759.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:40 | TRO3.23 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.23 | 2016-09-27 | OK | BON | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. MARTIN Jean-Claude | c9404f210692su85671_20170927083959.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 16:43 | ?4 | Industriel | etage cote nord |  | ligne de manutention de charges palettisees | ? | 2017-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927164303.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 16:47 | E1B5.12.1.5 | Industriel | Etage |  | PA1103 | E1B5.12.1.5 | 2017-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927164714.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:27 | ?5 | Industriel | etage cote nord |  | PA1053 | ? | 2017-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927172630.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:30 | E1B5.D13 | Industriel | Etage |  | PA1259 | E1B5.D13 | 2016-06-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927172953.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:36 | F1A3.3 | Industriel | Etage | ESCALIER PRES MC3 - POTEAU 20B | AEROTHERMES RECEPTION EXPEDITION MP | F1A3.3 | 2016-07-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | D2 consigne ,aerotherme Z1.3 | [9 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927173625.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:39 | F1A17.15 | Industriel | Etage | CLIMATISEUR MAGASIN | Traitement d'air magasin reception AC | F1A17.15 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927173858.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:45 | E1B5 | Industriel | Etage | Près MC 3 | Éclairage + PC bureaux réception | E1B5 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927174423.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:06 | TRO3.2.4 | Industriel | Etage | Local Informatique | Coffret TRO3.2.4 | TRO3.2.4 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927180557.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:15 | ?6 | Industriel | etage |  | cta | F1A17/17 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927181446.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:18 | F1B10 | Industriel | Etage | Travée A matières premières | CTA Atelier de prelevement | F1B10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927181828.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:25 | F1A17.19 | Industriel | Etage |  | PA1223 | F1A17.19 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927182453.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:28 | E1B5.49 | Industriel | Etage |  | PA1125 | E1B5.49 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927182800.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:30 | F1A17.19 | Industriel | Etage |  | PA1224 + PA1224 | F1A17.19 | 2017-09-27 | OK | BON | [24 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927182919.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:35 | F3A32.11 | Industriel | etage |  | TA LOCAL DELIVRANCE SUCRE | F3A32.11 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927183522.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:38 | F3A32.10 | Industriel | Etage |  | PA1199 + PA1200 | F3A32.10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927183723.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:40 | F3A32.10 | Industriel | Etage |  | PA1199 | F3A32.10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927183938.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:48 | ?7 | Industriel | etage nord |  | sonde temperature magasin | tro3.1.11 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | NOK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927184355.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:53 | ?8 | Industriel | etage nord |  | chambre froide 2-8 degres rideaux rapide | f3a32.17 | 2017-09-27 | NOK | BON | SO | OK | OK | OK | OK | NOK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927185254.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:10 | ?9 | Industriel | etage | rideaux rapide acces Glatt8 | PA | ? | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927191021.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:20 | ?10 | Industriel | etage | zone technique glatt8 | coffret electrique Fike 6PE _1_1 | ? | 2017-09-27 | NOK | BON | SO | NOK | OK | OK | OK | NOK | NOK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927192009.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:24 | ?11 | Industriel | etage | local technique glatt 8 | armoire contrôle commande système 11EL_1_1 | tro3.29.10 |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927192420.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:29 | ?12 | Industriel | etage | local technique glatt 8 | cta | f8.21.17 d17 |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927192835.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:32 | ?13 | Industriel | etage | local technique glatt8 | système de contrôle LIE | ? |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927193146.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:36 | F8A21.17 | Industriel | ETAGE | Zone technique | cta process glatt8 | F8A21.17 |  | NOK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927193605.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:44 | F3A10.16 | Industriel | Etage | au dessus box de pesée | box peseée 5 | F3A10.16 | 2017-09-29 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29 | M. MARTIN Jean-Claude | c9404f210692su85671_20170929124401.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:54 | F3A10.19 | Industriel | Etage | Au dessus Box 4 | FLUX LAMINAIRE BOX N° 4 | F3A10.19 | 2016-09-29 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29 | M. MARTIN Jean-Claude | c9404f210692su85671_20170929125406.jpg
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:58 | F3A10.35 | Industriel | Etage | Au dessus du BOX 2 | BOX2 | F3A10.35 | 2016-09-29 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29 | M. MARTIN Jean-Claude | c9404f210692su85671_20170929125810.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:25 | F3A17 | Industriel | Etage | ZT SUD | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-09-22 | OK | BON | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22 | M. MARTIN Jean-Claude | c9404f210692su85671_20171002202446.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:29 | F3A32.14 | Industriel | Etage | STOKAGE | TRAITEMENT D'AIRE CM1042 | F3A32.14 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | NOK | OK | OK | serrure legrand absent | [9 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927184355.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:30 | ?14 | Industriel | cote nord | bureaux local informatique |  | E1B5.40 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-09-27 | M. LEROY Emmanuel | c9404f210692su85671_20170927180355.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:35 | F4A9 | Administratif | ETAGE | CUISINE DIRECTION | TD CUISINE DIRECTION | F4A9 | 2016-09-04 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | vérifier si la consignation datant depuis 2013 est toujours d'actualité | relier la porte a la terre | [8 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004183507.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:42 | E4A10 | Administratif | Etage | COULOIR DIRECTION | eclairage+PC direction | E4A10 | 2016-09-04 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004184219.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:46 | TRO3.5 | Administratif | ETAGE | COULOIR DIRECTION | PC ONDULE | TRO3.5 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004184616.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:02 | F4A9.7 | Administratif | ETAGE | SALLE REUNION DIRECTION MEZZ 1 | TD ZONE | F4A9.7 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004185800.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:08 | E4A12 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A12 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004190811.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:11 | TRO3.22 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.22 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04 | M. MARTIN Jean-Claude | c9404f210692su85671_20171004191037.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 20:49 | F7A11.13.1 | Platine | Etage | ZT SUD | FLUX LUMINAIRES WEISS | F7A11.13.1 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005204924.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:04 | TRO4.1.2 | Platine | Etage | Technique EST | TD ONDULE R+1 REP12 | TRO4.1.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | mettre les plans à jour | [9 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005210402.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:08 | F7A11 | Platine | ETAGE | Zone technique étage Sud-Est | TD R+1-3 REP15 | F7A11 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005210803.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:11 | F7A11.12 | Platine | Etage | Technique EST | MELANGEUR VRIECO PLAVIX | F7A11.12 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005211058.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:19 | F7A11.13.2 | Platine | Etage | Technique EST | CALIBREUR + POMPE A POUDRE E37 | F7A11.13.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005211907.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:21 | F7A11.13.3 | Platine | Etage | Technique EST | CALIBREUR CLOPI LOCAL e33 + COMPACTAGE r32 | F7A11.13.3 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005212049.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:25 | F7A11.13.4 | Platine | ETAGE | LT E81 | CALIBRAGE OSCILLANT FREWIT CLOPI E3 | F7A11.13.4 | 2016-09-05 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Armoire consignés depuis 2007 | [9 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005212519.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:32 | F7A11.13.4.D9 | Platine | Etage | Zone technique EST | Mat GERBEURS | F7A11.13.4.D9 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Armoire hors tension équipement désengager | [9 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005213211.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:35 | F7A11.13.3.D21 | Platine | Etage | Technique EST | MAT ROTATIF | F7A11.13.3.D21 | 2016-09-05 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Voyant sous tension a changer | [9 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005213519.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:46 | F7A11.13.2.D21 | Platine | Etage | Technique EST | COFFRET MAT ROTATIF | F7A11.13.2.D21 | 2016-09-05 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Q3 consignés | Remplacé le voyant sous tension 24v | [8 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005214608.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:44 | F3A10.18 | Industriel | Etage |  | FLUX LAMINAIRE BOX N° 3 | F3A10.18 | 2016-09-02 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | [10 empty] | OK | 2017-10-02 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005224415.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:46 | TRO4.1.2 | Platine | Etage | Technique EST | TD ONDULE R+1 REP12 | TRO4.1.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005224550.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:47 | F7A10.13.5 | Platine | Etage | ZONE TECHNIQUE SUD | table elevatrice aprovel | F7A10.13.5 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005224702.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:48 | F7A10.13.1 | Platine | Etage | ZONE TECHNIQUE SUD | DEPOTAGE CALIBRAGE IRBESARTAN | F7A10.13.1 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005224822.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:50 | F7A10.13.1.D21 | Platine | Etage | ZONE TECHNIQUE SUD | Mat Rotative | F7A10.13.1.D21 | 2016-09-05 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05 | M. MARTIN Jean-Claude | c9404f210692su85671_20171005224931.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:25 | F7A10.13.1 | Platine | Etage | ZONE TECHNIQUE SUD | DEPOTAGE CALIBRAGE IRBESARTAN | F7A10.13.1 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006182501.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:35 | F7A21.1 | Platine | Etage | ZONE TECHNIQUE SUD | CTA PLAVIX | F7A21.1 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006183447.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:41 | F7A21 | Platine | Etage | ZONE TECHNIQUE SUD | ARMOIRE DISTRIBUTION CTA + DEPOUSSIEREUR | F7A21 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006184036.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:46 | F7A10 | Platine | ETAGE | Zone technique étage .SUD | ARMOIRE DISTRIBUTION | F7A10 | 2016-09-06 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | F7A10.8 Consignés (alim sirène porte) | [9 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006184246.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:54 | F7A21.2 | Platine | Etage | ZT SUD | CTA1.1 | F7A21.2 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006185144.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:11 | F7A18.D3 | Platine | Etage | ZONE Technique SUD Local Dpoussieureures D3 D4 | DEPOUSSIEUR UD3 1083 | F7A18.D3 | 2016-10-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | [15 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006191126.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:28 | F7A21.3 | Platine | Etage | ZONE TECHNIQUE SUD | CTA | F7A21.3 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006191857.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:29 | F7A21.6 | Platine | ETAGE | LT E80 E80.7 | DEPOUSSIEREURE D7 | F7A21.6 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006191658.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:30 | F7A21.5 | Platine | ETAGE | LT E80 E80.3 | depousierreur D6 | F7A21.5 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006191541.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:31 | F7A21.4 | Platine | ETAGE | LT E80 E80.1 | depoussierreur D5 | F7A21.4 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | NOK | SO | OK | OK | OK | OK | OK | OK | OK | Mettre les plans dans l'armoire | [9 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006191354.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:34 | F7A10.13.2.D21 | Platine | Etage | ZONE TECHNIQUE SUD | MAT ROTATIF | F7A10.13.2.D21 | 2016-09-06 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Changer le voyant sous tension | [9 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006193356.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:47 | TRO4.1.2.12 | Platine | Etage | Zone technique SUD | ZT-R81-GTC | TRO4.1.2.12 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06 | M. MARTIN Jean-Claude | c9404f210692su85671_20171006194658.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 17:58 | F3A32.11 | Industriel | etage |  | TA LOCAL DELIVRANCE SUCRE | F3A32.11 | 2017-10-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016175828.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 18:02 | F3A32.10 | Industriel | Etage |  | PA1200 | F3A32.10 | 2017-10-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016180204.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 19:38 | F8A21.17 | Industriel | ETAGE | Zone technique ouest | TD chargeur | F8A21.17 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | il faut fermer les ouvertures dans le plastron du bas | [9 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016193821.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 19:41 | F8A21.9 | Industriel | Etage | ZT Ouest | CTA GRAB 2B, LOCAL CHARGE, BUREAUX | F8A21.9 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016194058.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 20:12 | F8A20 | Industriel | Etage | ZT OUEST | ZONE TECHNIQUE ETAGE FONCTIONS SUPPORT | F8A20 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016201209.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 20:17 | F8A20.3 | Industriel | Etage | ZT FONCTIONS SUPPORT | CTA GELLULEUSES 1 & 2 | F8A20.3 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016201635.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:21 | F8A16.6.1 | Industriel | Etage | Local delivrance sucre | CE1001 | F8A16.6.1 | 2016-07-16 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016212053.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:38 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016213809.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:39 | F1A17.12 | Industriel | Etage | CENTRALE PRELEVEMENT | CENTRALE PRELEVEMENT | F1A17.12 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016213928.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:54 | F1A17.5 | Industriel | Etage | Box prelevement 2 | Box prelevement 2 | F1A17.5 | 2016-09-16 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | voir a changer le ventilateur | changer le voyant sous tension | [8 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016215414.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:57 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016215727.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:15 | F1A17.21.3 | Industriel | Etage | QUAI NORD | PA1102 | F1A17.21.3 | 2016-07-16 | OK | MOYEN | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | Il faut mettre les plans dans le coffret | [9 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016221438.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:21 | F1A17.15 | Industriel | Etage | CLIMATISEUR MAGASIN | Traitement d'air magasin reception AC | F1A17.15 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016221953.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:23 | F1A3.3 | Industriel | Etage | ESCALIER PRES MC3 - POTEAU 20B | AEROTHERMES RECEPTION EXPEDITION MP | F1A3.3 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016222302.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:25 | E1B5 | Industriel | Etage | Près MC 3 | Éclairage + PC bureaux réception | E1B5 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171016222448.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-18 22:30 | F1B10 | Industriel | Etage | Travée A matières premières | CTA Atelier de prelevement | F1B10 | 2016-08-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16 | M. MARTIN Jean-Claude | c9404f210692su85671_20171018223026.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-18 22:37 | F1A17.17 | Industriel | Etage | RECEPTION MP | PA2082 | F1A17.17 | 2016-09-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-18 | M. MARTIN Jean-Claude | c9404f210692su85671_20171018223712.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:27 | F7A9 | Platine | Etage | Zone technique étage .NORD EST | TD R+1-1 REP13 | F7A9 | 2016-09-19 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | DT40 F7A9.14.4 Alim porte tirette sud coupé avec un cadenas numero 8 | Refaire la cosse de terre sur la porte | Voynt sur la porte non raccorde6 | [7 empty] | OK | 2017-10-19 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020172619.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:31 | F7A9.14.3 | Platine | Etage | magasin Platine | PA 2024 | F7A9.14.3 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020173037.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:37 | F7A9.14.2 | Platine | Etage | magasin Platine | PA 2023 | F7A9.14.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020173706.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:47 | TRO4.1.2.4 | Platine | Etage | Magasin | Yokogawa température | TRO4.1.2.4 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | [11 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020174645.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 18:28 | F7A11.13.7 | Platine | ETAGE | Stockage MATERIEL | TDE92 | F7A11.13.7 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | Il faut dégagée devant l'armoire | [9 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020182824.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 18:44 | F7A11.7 | Platine | ETAGE | ENTREE PLATINE | COFFRET VENTOUSE | F7A11.7 | 2017-10-20 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | Coffret très haut il faut l'échelle pour y accéder | [9 empty] | NOK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020184329.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 21:30 | E1B5.49 | Industriel | Etage |  | PA1125 | E1B5.49 | 2017-10-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020212831.jpg
MARTIN | Jean-Claude |  |  |  | 2017-10-20 21:34 | F3A32.14 | Industriel | Etage | STOKAGE | TRAITEMENT D'AIRE | F3A32.14 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | manque serrure | [9 empty] | OK | 2017-10-20 | M. MARTIN Jean-Claude | c9404f210692su85671_20171020213145.jpg
[13 empty] | BON BON BON BON: NON FAITE | [11 empty] | 2017-11-01
2017-12-01
2018-01-01
2018-02-01
2018-03-01
2018-04-01
2018-05-01

## Graphique général
Nombre de Sélectionner l'armoire concernée | ETAT GENERAL DES MACHINES
MOIS | BON | MAUVAIS | MOYEN | OBSOLETE | Total général
juin | 25 | 1 | 1 |  | 27
juil | 58 | 1 | 7 | 2 | 68
août | 8 |  |  |  | 8
sept | 127 | 1 | 1 | 1 | 130
oct | 56 |  | 2 |  | 58
ETAT GENERAL DES MACHINES
| Total à réaliser | BON | MAUVAIS | MOYEN | OBSOLETE | Total réalisé | Restant à réaliser | Avancement
juin | 96 | 25 | 1 | 1 | 0 | 27 | 1125 | 28.12%
juil | 96 | 58 | 1 | 7 | 2 | 68 | 1084 | 70.83%
août | 96 | 8 | 0 | 0 | 0 | 8 | 1144 | 8.333%
sept | 96 | 127 | 1 | 1 | 1 | 130 | 1022 | 135.4%
oct | 96 | 56 | 0 | 2 | 0 | 58 | 1094 | 60.42%
nov | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
déc | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
janv | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
févr | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
mars | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
avr | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%
mai | 96 | 0 | 0 | 0 | 0 | 0 | 1152 | 0%

## JUIN
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle
MARTIN | Jean-Claude |  |  |  | 2017-06-07 11:42 | E1B17 | Industriel | Sous-sol | Éclairage et PC mise en fûts | Éclairage et PC mise en fûts |  | 2017-06-07 | OK | MAUVAIS | NOK | OK | NOK | OK | NOK | NOK |  | OK | [16 empty] | OK | 2017-06-07
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:54 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:18 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:49 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | voyant présence tension fusible2A HS | voyant présence tension led ref ZBV-M1 HS |  |  |  |  | remplacement des fusibles ok |  |  |  | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 17:45 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:37 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | voyant présence tension Hs réf 230v 20ma | [9 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-15 15:51 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 |  | 2017-06-14 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | SANS OBJET | OK |  | OK | SANS OBJET | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:16 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER | F3A10.20 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:24 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 | F3A15 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:27 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 | F3A28.1 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:29 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 | TRO2.1.8.12 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:30 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 | TRO2.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:50 | TRO2.1.8.13 | Industriel | Etage | LT SUD LIPANOR | GTC ZT LIPANOR | TRO2.1.8.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:53 | F6A2 | Industriel | Etage | ZT SUD | Atelier DEPAKINE GLATT4 | F6A2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | SANS OBJET | OK | OK | OK | OK | OK | [10 empty] | NOK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:58 | F6A2.2 | Industriel | Etage | ZT Sud | CTA GLATT 4 | F6A2.2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK |  | OK | NOK | OK | OK | OK | OK | OK | filtre de la ventilation son sale | [8 empty] | remplacement des filtre ok | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:02 | F3A15.1 | Industriel | Etage | ZT SUD LIPANOR | PMA800 FIELDER 7 PUISSANCE | F3A15.1 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:17 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 | TRO2.1.8.17 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:57 | F3A20.13.11 | Industriel | Etage | LT SUD LIPANOR | CTA LIPANOR | F3A20.13.11 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:02 | F3D2 | Industriel | Etage | ZT Sud | Puissance Granulateur Fielder Laf 2 | F3D2 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:08 | TRO2.1.8.5 | Industriel | Etage | ZT Sud | Automatisme FIELDER. LAF2 granulateur | TRO2.1.8.5 | 2016-06-16 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:26 | F3A20.12 | Industriel | Etage | ZT SUD | CA 1019 | F3A20.12 | 2016-08-15 | OK | MOYEN | NOK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:35 | F3A11 | Industriel | Etage | ZT SUD | CA 1006 CLIM TRANXENE | F3A11 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:43 | F3D9.5 | Industriel | Etage | ZT SUD | CTA LAF 5 | F3D9.5 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:52 | TRO2.1.16 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD GTC | TRO2.1.16 | 2016-08-18 | OK | BON | OK | OK | SO | OK | OK | NOK | NOK | OK | SO | OK | NOK | OK | OK | OK | plastron enlevé suite a la thermographie mais remis en place | [8 empty] | remise en place des plastrons | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 19:13 | TRO2.1 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD PLATEAU INDUS | TRO2.1 | 2016-08-26 | OK | BON | OK | OK | SO | OK | OK | OK | NOK | OK | SO | OK | NOK | OK | OK | OK | plan a remettre à jour | manque obturateurs | [8 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:28 | F3A10 | Industriel | Etage | ZT SUD | Distribution divers | F3A10 | 2016-08-26 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | prevoir nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:31 | F3D9 | Industriel | Etage | ZT SUD | Distribution divers | F3D9 | 2016-08-23 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir le nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30

## Graphique JUIN
ETAT GENERAL DES MACHINES
| Total à réaliser | BON | MAUVAIS | MOYEN | OBSOLETE | Total réalisé | Restant à réaliser | Avancement
juin | 96 |  |  |  |  | 0 | 1152 | 0%

## JUILLET
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle
MARTIN | Jean-Claude |  |  |  | 2017-06-07 11:42 | E1B17 | Industriel | Sous-sol | Éclairage et PC mise en fûts | Éclairage et PC mise en fûts |  | 2017-06-07 | OK | MAUVAIS | NOK | OK | NOK | OK | NOK | NOK |  | OK | [16 empty] | OK | 2017-06-07
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:54 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:18 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 19:49 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | voyant présence tension fusible2A HS | voyant présence tension led ref ZBV-M1 HS |  |  |  |  | remplacement des fusibles ok |  |  |  | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 17:45 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 |  | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-14 18:37 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 |  | 2017-06-14 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | voyant présence tension Hs réf 230v 20ma | [9 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-15 15:51 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 |  | 2017-06-14 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | SANS OBJET | OK |  | OK | SANS OBJET | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:16 | F3A10.20 | Industriel | Etage | LT SUD LIPANOR | WP 150 TRAITEMENT AIR FIELDER | F3A10.20 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:24 | F3A15 | Industriel | Etage | ZT SUD | Éclairage + PC fielder 7 | F3A15 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:27 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 | F3A28.1 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:29 | TRO2.1.8.12 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE LAF 4 | TRO2.1.8.12 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:30 | TRO2.13 | Industriel | ETAGE | LT SUD LIPANOR | SECOURUE FIELDER 7 | TRO2.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:50 | TRO2.1.8.13 | Industriel | Etage | LT SUD LIPANOR | GTC ZT LIPANOR | TRO2.1.8.13 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:53 | F6A2 | Industriel | Etage | ZT SUD | Atelier DEPAKINE GLATT4 | F6A2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | SANS OBJET | OK | OK | OK | OK | OK | [10 empty] | NOK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 18:58 | F6A2.2 | Industriel | Etage | ZT Sud | CTA GLATT 4 | F6A2.2 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK |  | OK | NOK | OK | OK | OK | OK | OK | filtre de la ventilation son sale | [8 empty] | remplacement des filtre ok | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:02 | F3A15.1 | Industriel | Etage | ZT SUD LIPANOR | PMA800 FIELDER 7 PUISSANCE | F3A15.1 | 2017-06-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:17 | TRO2.1.8.17 | Industriel | Etage | LT SUD LIPANOR | AUTOMATE FIELDER7, PMA 800 | TRO2.1.8.17 | 2016-06-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-14
MARTIN | Jean-Claude |  |  |  | 2017-06-16 19:57 | F3A20.13.11 | Industriel | Etage | LT SUD LIPANOR | CTA LIPANOR | F3A20.13.11 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:02 | F3D2 | Industriel | Etage | ZT Sud | Puissance Granulateur Fielder Laf 2 | F3D2 | 2016-06-16 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-16 20:08 | TRO2.1.8.5 | Industriel | Etage | ZT Sud | Automatisme FIELDER. LAF2 granulateur | TRO2.1.8.5 | 2016-06-16 | OK | BON | OK | OK | SANS OBJET | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-16
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:26 | F3A20.12 | Industriel | Etage | ZT SUD | CA 1019 | F3A20.12 | 2016-08-15 | OK | MOYEN | NOK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:35 | F3A11 | Industriel | Etage | ZT SUD | CA 1006 CLIM TRANXENE | F3A11 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:43 | F3D9.5 | Industriel | Etage | ZT SUD | CTA LAF 5 | F3D9.5 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation filtre doit être remplacé | [9 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 18:52 | TRO2.1.16 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD GTC | TRO2.1.16 | 2016-08-18 | OK | BON | OK | OK | SO | OK | OK | NOK | NOK | OK | SO | OK | NOK | OK | OK | OK | plastron enlevé suite a la thermographie mais remis en place | [8 empty] | remise en place des plastrons | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 19:13 | TRO2.1 | Industriel | ETAGE | ZT SUD | ZT ETAGE SUD PLATEAU INDUS | TRO2.1 | 2016-08-26 | OK | BON | OK | OK | SO | OK | OK | OK | NOK | OK | SO | OK | NOK | OK | OK | OK | plan a remettre à jour | manque obturateurs | [8 empty] | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:28 | F3A10 | Industriel | Etage | ZT SUD | Distribution divers | F3A10 | 2016-08-26 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | prevoir nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-06-30 20:31 | F3D9 | Industriel | Etage | ZT SUD | Distribution divers | F3D9 | 2016-08-23 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir le nettoyage de l armoire | [8 empty] | armoire nettoyer | OK | 2017-06-30
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:25 | F3A10.2 | Industriel | Etage | ZT SUD | PC + divers LAF 5 | F3A10.2 | 2016-08-12 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | disjoncteur tombée F3A10.2.7 pc atelier 5 | [9 empty] | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.2.2 | Industriel | Etage | ZT SUD | CMA LAF 5 | F3A10.2.2 | 2016-08-12 | OK | BON | OK | OK | OK |  | OK | OK | OK |  | SO | OK | NOK | OK | OK | OK | manque cache goulotte | [8 empty] | mise en place d'un cache goulotte | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.21 | Industriel | Etage | ZT SUD | CMA LAF 1 | F3A10.21 | 2016-08-12 | OK | OBSOLETE | NOK | OK | SO | SO | SO | SO | SO | SO | SO | OK | SO | OK | OK | OK | armoire consigné mise l'arrêt complet | [9 empty] | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A20.8.1 | Industriel | Etage | ZT SUD | Retournement + variateur LAF 1 | F3A20.8.1 | 2016-08-12 | OK | OBSOLETE | NOK |  | SO | OK | OK | OK | OK | SO | SO | OK | SO | OK | OK | OK | général armoire disjonter | [9 empty] | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.2.1 | Industriel | Etage | ZT SUD | Variateur pompes LAF 5 | F3A10.2.1 | 2016-08-12 | OK | MOYEN | OK | OK | OK | NOK | OK | NOK | NOK | OK | NOK | OK | OK | OK | OK | OK | armoire très sale | manque plan | prévoir le remplacement du filtre | [6 empty] | nettoyage de l'armoire | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | TRO2.1.15 | Industriel | Etage | ZT SUD | FIELDER 5 SECOURU automate | TRO2.1.15 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | NOK | OK | OK | OK | grille de ventilation cassé prévoir a la remplacer | manque cache goulotte | [8 empty] | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-12 21:26 | F3A10.3 | Industriel | Etage | ZT SUD | FIELDERS 5 PUISSANCE | F3A10.3 | 2016-08-12 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prevoir le remplacement des filtres | prévoir le nettoyage de l'armoire | [7 empty] | remplacement des filtres de ventilation et nettoyage de l'armoire | OK | 2017-07-12
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:37 | TRO2.1.5 | Industriel | Etage | ZT SUD | LAF 5 SECOURU automate | TRO2.1.5 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir nettoyage de l'armoire | [8 empty] | nettoyage de l'armoire le 13/07/2017 | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:37 | F3A10.8 | Industriel | Etage | ZT SUD | AUTOMATE LAF5 | F3A10.8 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | prévoir nettoyage de l'armoire | [8 empty] | nettoyage de l'armoire le 13/07/2017 | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3A17 | Industriel | Etage | ZT SUD | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-08-13 | OK | BON | OK | OK | SO | NOK | OK | NOK | NOK | OK | SO | OK | NOK |  | SO | OK | prévoir nettoyage de l'armoire | manque plan | manque obturateur | [6 empty] | nettoyage de l'armoire ,remise en place des obturateurs | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3A20.8 | Industriel | Etage | ZT SUD | EXTRACTION/VENTILATION LAF 1 | F3A20.8 | 2016-08-13 | OK | MOYEN | NOK | OK | SO | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | général de l'armoire est a l'arrêt | [9 empty] | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3D9.1 | Industriel | Etage | ZT SUD | FIELDER LAF 3 | F3D9.1 | 2016-08-13 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | F3D9.1.2 | Industriel | Etage | ZT SUD | CMA LAF 3 | F3D9.1.2 | 2016-08-13 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | [10 empty] | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:50 | TRO2.1.3 | Industriel | Etage | ZT SUD | LAF 3 AUTOMATE | TRO2.1.3 | 2016-08-13 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage des filtres de ventilation | [8 empty] | nettoyage des filtres de la ventilation | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:51 | F3A20.11.1 | Industriel | Etage | ZT SUD | LAF 3 AUTOMATE | F3A20.11.1 | 2016-08-13 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir remplacement voyant ref ZBV-M1 230v | prévoir le nettoyage des filtres de la ventilation | [7 empty] | nettoyage des filtres de la ventilation | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-13 20:51 | F3D9.1.1 | Industriel | ETAGE | ZT SUD | Variateur FIELDER LAF 3 | F3D9.1.1 | 2016-08-13 | OK | BON | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage de l'armoire | prévoir le remplacement des filtres ventilation | [7 empty] | nettoyage de l'armoire,remplacement des filtres de la ventilation | OK | 2017-07-13
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:29 | F1A17 | Industriel | Etage | ALIM ZONE | ALIM ZONE | F1A17 | 2016-08-17 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:30 | TRO3.2.10 | Industriel | Etage | RECEPTION MP | GTC etage nord | TRO3.2.10 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:31 | F1A17.13 | Industriel | Etage | RECEPTION | WESPACKS reception MP | F1A17.13 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:31 | F1A17.17 | Industriel | Etage | RECEPTION MP | PA2082 | F1A17.17 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:32 | F1B10.6 | Industriel | Etage | RECEPTION MP | aerothermes quai reception | F1B10.6 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:33 | TRO3.2.5 | Industriel | Etage |  | Arrosage Sprinkler exterieur portakabin | TRO3.2.5 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:34 | F1A24.2 | Industriel | Etage | Quai nord | PA PORTES NOMAFA ETAGE RECEPTION | F1A24.2 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:34 | F1A24.2.1 | Industriel | Etage | RECEPTION MP | PA1054 PA1053 | F1A24.2.1 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:35 | F1A17.21 | Industriel | Etage | QUAI NORD | PC eclairage chargeurs rideaux | F1A17/21 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-19 08:35 | F1A17.21.21 | Industriel | Etage | CONVOYEUR RECEPTION | CONVOYEUR RECEPTION | F1A17.21.21 | 2016-08-17 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-17
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:34 | F1B22 | industriel | Etage | Travée B matières premières | CA 1067 | F1B22 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | disjoncteur thermique Q13 consigne | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:35 | F1A17.5 | Industriel | Etage | Box prelevement 2 | Box prelevement 2 | F1A17.5 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:38 | F1A17.26 | Industriel | Etage |  | Coffret banderoleuse | F1A17.26 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:38 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:44 | ?1 | Industriel | Sous-sol nord | Clim poste 1 | Coffret détection feu | ? | 2016-08-20 | OK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | OK | pas numero d'armoire | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-21 09:48 | F1A17.12 | Industriel | Etage | CENTRALE PRELEVEMENT | CENTRALE PRELEVEMENT | F1A17.12 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:57 | F1A17.21.2.11 | Industriel | Etage |  | porte 7 quai nord | F1A17.21.2.11 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:58 | F1A17.21.2.3 | Industriel | Etage |  | PA2106 (porte n°7) | F1A17.21.2.3 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 15:59 | F1A17.9.6.4 | Industriel | Etage |  | Pont hydraulique (porte n°6) | F1A17.9.6.4 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:00 | F1A17.21.22 | Industriel | Etage |  | rideau rapide nergeco | F1A17.21.22 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:00 | F1A17.21.2.4 | Industriel | Etage |  | PA2105 (porte n°6) | F1A17.21.2.4 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:01 | ?2 | Industriel | etage | quai nord | coffret gestion interverrouillage porte quai | ? | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:02 | F1A17.21.2.11 | Industriel | Etage |  | rideau rapide nergeco | F1A17.21.2.11 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:03 | F1A17.21.2.10 | Industriel | Etage | QUAI NORD | Coffret gestion SAS magasin | F1A17.21.2.10 | 2016-08-20 | OK | BON | SO | OK | OK | OK |  | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:03 | F1A17.21.2 | Industriel | Etage | QUAI NORD | Armoire rideaux | F1A17.21.2 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:04 | F1A17.21.22 | Industriel | Etage |  | table elevatrice | F1A17.21.22 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:04 | F1A17.18 | Industriel | Etage | quai nord | coffret electro aimant | F1A17.18 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:05 | F1A17.21.2.5 | Industriel | Etage | quai nord | PA2104 (porte n°5) | F1A17.21.2.5 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:06 | F1A17.9.6.6 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.6 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:06 | F1A17.21.2.6 | Industriel | Etage | quai nord | PA2103 (porte n°4) | F1A17.21.2.6 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:07 | F1A17.21.2.7 | Industriel | Etage |  | Pont Hydraulique PA2102 (porte n°3) | F1A17.21.2.7 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:07 | F1A17.21.2.7 | Industriel | Etage | quai nord | Pont Hydraulique PA2102 (porte n°3) | F1A17.21.2.7 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:08 | F1A17.9.6.8 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.8 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:08 | F1A17.21.2.8 | Industriel | Etage | quai nord | PA2101 | F1A17.21.2.8 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:09 | ?3 | Industriel | etage | quai nord | PA1202 | ? | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | NOK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:09 | F1A17.9.6.9 | Industriel | Etage | QUAI NORD | PONT HYDRAULIQUE | F1A17.9.6.9 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-24 16:10 | E1B5.12 | Industriel | Etage | RECEPTION G25 | quai nord | E1B5.12 | 2016-08-20 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-07-20
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:54 | F3A10.15 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR PMA 800 | F3A10.15 | 2016-07-25 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK |  | OK | OK | prevoire le remplacement des filtres | prevoire le remplacement de l'éclairage de l'armoire ref 2*7w cft/827 2b | [8 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:54 | TRO2.1.8.2 | Industriel | Etage | LT SUD LIPANOR | MELANGEUR AUTOMATE FIELDER4 | TRO2.1.8.2 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:55 | F3A28.2 | Industriel | Etage | LT SUD LIPANOR | ARMOIRE PUISSANCE LAF 4 | F3A28.2 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | ventilation Hs prevoire remplacement ventilateur | [9 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 15:55 | F3A28.3 | Industriel | Etage | ZT Sud | atelier laf 4 calibreur CMA / PEROLO LAF 4 | F3A28.3 | 2016-07-25 | OK | BON | OK | OK | NOK | OK | OK | NOK | NOK |  | OK | OK | OK | OK | OK | OK | voyant marche calibreur hs ref 24v 125ma | manque plan | [7 empty] | remplacent du voyant 24v le 25/07/2017 | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:00 | F3A28 | Industriel | Etage | ZT Sud | FIELDER LAF 4 | F3A28 | 2016-07-25 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | voyant hs et fusible | manque obturateur | [8 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:01 | TRO2.1.8 | Industriel | Etage | ZT SUD LIPANOR | COFFRET ETAGE ZT SUD | TRO2.1.8 | 2016-07-25 | OK | BON | OK | OK | SO | OK | OK | OK | NOK | OK | SO | OK | OK | OK | OK | OK | mettre a jours le plan | [9 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:02 | F3A20.6 | Industriel | Etage | LT SUD LIPANOR | Éclairage + PC LIPANOR | F3A20.6 | 2016-07-25 | OK | BON | NOK | OK | OK | OK | NOK | OK | OK | OK | SO | OK | OK | OK | OK | OK | disjoncteur couper D12,D14,D15,D16 | sortie de cable reste des cables couper dans chemin de cable et brancher au bornier | [8 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-26 16:03 | F3A15.1 | Industriel | Etage | ZT SUD LIPANOR | PMA800 FIELDER 7 PUISSANCE | F3A15.1 | 2016-07-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | manque plan | [9 empty] | OK | 2017-07-25
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A21.7.16 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR WP170 RDC SAS PS | F3A21.7.16 | 2016-07-26 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | porte document arracher prévoir de le remettre | [8 empty] | remise en place du porte document le 26/07/2017 | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A20.13.26 | Industriel | Etage | LT SUD LIPANOR | COFFRET SAS PERSONNEL IMA 6 LIPANOR | F3A20.13.26 | 2016-07-26 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | SO | OK | OK | OK | SO | OK | [10 empty] | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A28.1 | Industriel | Etage | LT SUD LIPANOR | PUISSANCE LAF4 | F3A28.1 | 2016-07-26 | OK | MAUVAIS | OK | OK | SO | NOK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | armoire très sale prévoir le nettoyage | [8 empty] | nettoyage e l'armoire le 26/7/2017 | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:44 | F3A20.9 | Industriel | Etage | ZT SUD | puissance LAF2 | F3A20.9 | 2016-07-26 | OK | MOYEN | OK | OK | NOK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | voyant retourneur en service hs 24v | moteur ventilation ne fonctionne plus prevoire le remplacement | prevoire le nettoyage de l'armoire | [6 empty] | nettoyage de l'armoire et remplacement du voyant le2 6/07/2017 | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | TRO2.1.2 | Industriel | Etage | Local technique LAF 2 / 4 | Automatisme LAF 2 | TRO2.1.2 | 2016-07-26 | OK | MOYEN | OK | OK | OK | NOK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir le nettoyage de l'armoire | prévoir le remplacement des 2 moteur de ventilation | [7 empty] | nettoyage de l'armoire le 26/07/2017 | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | Industriel | Etage | ZT SUD | Retourneur laf 2 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | 2016-07-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-26
MARTIN | Jean-Claude |  |  |  | 2017-07-27 19:45 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | Industriel | Etage | ZT SUD | Retourneur laf 2 | F3A20.9 (repris sur répartiteur puissance F3A20.9) | 2016-07-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-07-26

## Graphique JUILLET
ETAT GENERAL DES MACHINES
| Total à réaliser | BON | MAUVAIS | MOYEN | OBSOLETE | Total réalisé | Restant à réaliser | Avancement
juin | 96 | 10 | 5 | 6 | 0 | 21 | 1131 | 21.88%
juillet | 96 | 2 | 1 | 2 | 1 | 6 | 1146 | 6.25%

## AOUT
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:42 | F3A20.11 | Industriel | Etage | ZT SUD | Retourneur et ventillateur LAF 3 | F3A20.11 | 2016-08-21 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK |  | OK | OK | prevoire le nettoyage du filtre de la ventilation | [9 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:47 | F3D9.6 | Industriel | Etage | Technique Sud | LAF 5 +TRANXENE SECOURS RESEAU EAU GLYCOLEE | F3D9.6 | 2016-08-21 | OK | BON | NOK | OK | SO | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | disjoncteur général à l'arrêt | [9 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 19:52 | F3A20 | Industriel | Etage | ZT SUD | Distribution divers | F3A20 | 2016-08-21 | OK | BON | OK | OK | SO | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:11 | F3A20.4 | Industriel | Etage | ZT SUD | ATELIER LAF 3 CUVES MAXILASE/VICTU | F3A20.4 | 2016-08-21 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:26 | F3D3.2 | Industriel | Etage | ZT Sud Ouest | CTA LAF 1 | F3D3.2 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK |  | OK | OK | OK | prévoir remplacement des filtres ventilation | [9 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:40 | F3D3.3 | Industriel | Etage | ZT Sud Ouest | CA1120 DCE LAF 3 | F3D3.3 | 2016-08-21 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | disjoncteur Q12 disjoncté alim voyant | voyant non alimenter | [7 empty] | voir avec cofely pour alim voyant | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 20:56 | F3D3.1 | Industriel | Etage | ZT Sud Ouest | CTA LAF 2 | F3D3.1 | 2016-08-21 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | les voyants de signalisation de fonnctionnement et de de faut ne fonctionne pas cause la fixation du contacte est hs ref ZBE-205 telemecanique a remplacer | [9 empty] | OK | 2017-08-21
MARTIN | Jean-Claude |  |  |  | 2017-08-21 21:03 | F3D3.5 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT AIR box pesee 6 | F3D3.5 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | prévoir remplacement filtre ventilation | [9 empty] | OK | 2017-08-21

## SEPTEMBRE
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle
MARTIN | Jean-Claude |  |  |  | 2017-09-12 13:51 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2017-09-12 | OK | BON | [24 empty] | OK | 2017-09-12
MARTIN | Jean-Claude |  |  |  | 2017-09-12 13:58 | F3D3.3.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEREUR laf 3 | F3D3.3.3 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-12
MARTIN | Jean-Claude |  |  |  | 2017-09-13 08:02 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2016-08-12 | OK | BON | OK | OK | OK | OK | OK | OK | OK |  |  | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-12
MARTIN | Jean-Claude |  |  |  | 2017-09-13 08:36 | F3D3.2.3 | Industriel | Etage | ZT Sud | DCE LAF 1 | F3D3.2.3 | 2017-09-12 | OK | BON | NOK | OK | OK | OK | OK | OK | OK |  | SO | OK | OK | OK | OK | OK | Inter general de l'armoire est consigné depuis 05/07/2017 | Fils débranché dans l'armoire | [8 empty] | OK | 2017-09-12
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:01 | F3D3.4.3 | Industriel | Etage | ZT Sud Ouest | DCE LAF 5 | F3D3.4.3 | 2017-09-14 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | SO | SO | OK | OK | OK | OK | OK | remettre les schémas dans l'armoire | [9 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:03 | F3D3.7 | Industriel | Etage | ZT Sud Ouest | DCE GRANULATEUR CONTINU ud1100 | F3D3.7 | 2016-08-14 | OK | BON |  | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:04 | F3D3.4 | Industriel | Etage | ZT Sud Ouest | CTA LAF5 | F3D3.4 | 2016-08-14 | OK | BON |  | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | Il faut re fixer le porte plans | [9 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:07 | F3D3.6 | Industriel | Etage | ZT Sud Ouest | DCE CALIBRAGE 2 BOX 2 | F3D3.6 | 2016-08-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:10 | F3D4 | Industriel | Etage | ZT SUD OUEST | Distribution divers GLATT 2 | F3D4 | 2016-08-14 | OK | BON | OK |  | OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-15 12:12 | F3D5 | Industriel | Etage | ZT SUD OUEST | Glatt 6 | F3D5 | 2016-08-14 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | [10 empty] | OK | 2017-09-14
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:17 | F3A10.9 | Industriel | Etage | Zone technique LAF 1, 3, 5 TRAVEE D | ECL SALLE LAVAGE | F3A10.9 | 2016-08-18 | OK | BON | OK | OK | SO | OK | OK | NOK | SO | SO |  | OK | OK | OK | OK | OK | Remettre le plans dans le coffret | [9 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:20 | F3D3 | Industriel | Etage | ZT OUEST | Éclairage zone technique sud-ouest | F3D3 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | Mettre le schema a jour | [9 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:24 | F3D3.9 | Industriel | Etage | ZT OUEST | Distribution divers | F3D3.9 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | [10 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:27 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 2 | F3D4.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:30 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | ATELIER GLATT 2 MAXILASSE PELLICULAGE | F3D4.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:34 | F3D5.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 6 | F3D5.1 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | SO | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-18 22:42 | F3D10.6 | Industriel | Etage | ZT Sud | DCE box 5 UD1089 | F3D10.6 | 2016-08-18 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-19 16:20 | F3D5.2 | Industriel | Etage | ZT SUD | Distribution divers GLATT 6 | F3D5.2 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | SO | [16 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-19 16:21 | TRO2.3.21.2 | Industriel | Etage | ZT OUEST | automate Glatt 6 | TRO2.3.21.2 | 2016-08-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | [17 empty] | OK | 2017-09-18
MARTIN | Jean-Claude |  |  |  | 2017-09-19 21:59 | F3D3.9.9 | Industriel | Etage | ZT Sud Ouest | Alim coffret gestion DCE | F3D3.9.9 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:04 | TRO2.1.16 | Industriel | Etage | ZT SUD OUEST | ZT Ouest phase 1 GTC | TRO2.1.16 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | NOK |  | OK | OK | OK | OK | OK | OK | OK | mettre les schémas dans l'armoire | [9 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:07 | F3D9.3 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT D'AIR DEPAKINE BOX 6 | F3D9.3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:11 | F3A10.17.21 | Industriel | Etage | ZT SUD OUEST | SAS Rideau/Porte BOX PESEE | F3A10.17.21 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:17 | E3A3 | Industriel | Etage | Éclairage box de pesées | Éclairage box de pesées | E3A3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | Mise à jour les plans | [9 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:20 | F3A10.17 | Industriel | Etage | ZT OUEST | PC BOX PESEE | F3A10.17 | 2016-08-19 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:24 | TRO2.1.11 | Industriel | Etage | ZT Sud | DISTRIBUTION EAU PURIFIEE YOKOGAWA PROCESS | TRO2.1.11 | 2016-08-19 | OK | BON |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:26 | TRO2.2 | Industriel | ETAGE | ZT OUEST | SALLE INFOR. BOX PESEE | TRO2.2 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:30 | F3A10.17.25 | Industriel | Etage | ZT Sud | Boucle d'eau purifiée | F3A10.17.25 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:33 | F3D3.13 | Industriel | ETAGE | ZONE TECHNIQUE SUD | TRAITEMENT AIR GRANULATION CONTINU | F3D3.13 | 2016-08-19 | OK | BON | OK |  | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:35 | F3A10.17.29 | Industriel | Etage | ZT OUEST | CENTRALE DE PESAGE BOX 2 | F3A10.17.29 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-19 22:37 | F3A10.17.28 | Industriel | Etage | ZT OUEST | CENTRALE DE PESEE BOX 5,PROCESS | F3A10.17.28 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-20 17:19 | F3A10 | Industriel | Etage | ZT SUD | Distribution divers | F3A10 | 2016-08-20 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | D10 consigné depuis le 29/08/2016 | [8 empty] | voir si le depart 18 n'est plus utilisé de supprimer le cadenas est le mettre en Resrve | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 17:26 | F3D10.3 | Industriel | Etage | ZT ouest | CTA labo prod | F3D10.3 | 2016-08-20 | OK | BON | NOK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | Armoire cosigné depuis le 30/07/2015 par cofely | CTA en cours de démontage | [8 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:32 | F3D4.2 | Industriel | Etage | ZT Sud OUEST | Puissance GLATT 2 | F3D4.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:35 | TRO2.3.20.2 | Industriel | Etage | ZT SUD OUEST | PROCESS AUTOMATE GLATT 2 | TRO2.3.20.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:39 | F3D4.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 2 | F3D4.1 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:41 | F3D10.23 | Industriel | Etage | ZT Sud-Ouest | CTA BOX DE PESEE 2 | F3D10.23 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:42 | F3D10.25 | Industriel | Etage | ZT Sud-Ouest | DEPOUSSIERREUR BOX PESEE 1-2-3-4-5 | F3D10.25 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:44 | F3D9.3 | Industriel | Etage | ZT Sud Ouest | TRAITEMENT D'AIR DEPAKINE BOX 6 | F3D9.3 | 2016-08-20 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:46 | F3D10.16 | Industriel | Etage | ZT SUD | TRAITEMENT D'AIR LOCAUX POICONS | F3D10.16 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:48 | F3D5.1 | Industriel | Etage | ZT SUD OUEST | CTA GLATT 6 | F3D5.1 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:49 | F3D10.5 | Industriel | Etage | ZT Sud-Ouest | CTA BOX 5 | F3D10.5 | 2016-08-20 | OK | MAUVAIS | [14 empty] | A ncienne arrmoire consigné depuis 15/08/ 2015 | En cours de demontage | [8 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:51 | F3D10.24 | Industriel | Etage | ZT ouest | CTA BOX DE PESEE 1-3-4 | F3D10.24 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:56 | F3D10.5 | Industriel | Etage | ZT Sud-Ouest | CTA BOX 5 | F3D10.5 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Nouvelle Armoire box pesée No 5 | [9 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:58 | F3D10.2 | Industriel | Etage | ZT Sud-Ouest | TRAITEMENT AIR CELLULES COMPRESSIONS 9,10,11 | F3D10.2 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 20:59 | F3D10.22 | Industriel | Etage | ZT Sud-Ouest | UD1071 (DCE GELLULEUSE) | F3D10.22 | 2016-08-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:01 | F3D10.17 | Industriel | Etage | ZT SUD OUEST | DEPOUSSIREUR Accela cota | F3D10.17 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:03 | TRO2.1.16 | Industriel | Etage | ZT SUD OUEST | ZT Ouest phase 1 GTC | TRO2.1.16 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:04 | TRO2.3.20.2 | Industriel | Etage | ZT SUD OUEST | PROCESS AUTOMATE GLATT 2 | TRO2.3.20.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 21:08 | F3D3.1.3 | Industriel | Etage | ZT Sud Ouest | DEPOUSSIEUR LAF 2 | F3D3.1.3 | 2016-08-19 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-19
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:35 | F3D4.2 | Industriel | Etage | ZT Sud OUEST | Puissance GLATT 2 | F3D4.2 | 2016-09-20 | OK | BON | OK | [23 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:37 | F3F9.2 | Industriel | Etage | ZT ouest | PUISSANCE GLATT 5 | F3F9.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:38 | F3F9 | Industriel | Etage | ZT ouest | ALIM GENERALE GLATT 5 | F3F9 | 2016-09-20 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:40 | F3F9.1 | Industriel | Etage | ZT ouest | CTA GLATT 5 | F3F9.1 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-20 22:42 | F8A16.3 | Industriel | Etage | ZT OUEST | TRAITEMENT AIR GLATT 7 | F8A16.3 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-20
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:20 | F3D10.7 | Industriel | Etage | ZT ouest | Coffret Depoussiereur UD1070 | F3D10.7 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:21 | TRO3.7.13.3 | Industriel | Etage | ZT Ouest | Automatisme GLATT 5 | TRO3.7.13.3 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 17:53 | F3A32 | Industriel | Etage | ZT OUEST | Chambre froide, chambre deshy PC | F3A32 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:09 | F8A15 | Industriel | Etage | ZT OUEST | PUISSANCE GLATT 7 | F8A15 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:11 | TRO3.7.17 | Industriel | Etage | ZT Ouest | AUTOMATE GLATT 7 PROCESS | TRO3.7.17 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 18:16 | F3A32.1 | Industriel | Etage | ZT ouest | CTA CHAMBRE DESHYDRATEE | F3A32.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 20:44 | F3A10.10 | Industriel | Etage | MAINTENANCE MULTI PRODUIT | ATELIER REGLEURS MAINTENANCE | F3A10.10 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:02 | F3A10.4 | Industriel | Etage | BUREAU Opérateur Laveuse | STATION DE LAVAGE CONTAINERS | F3A10.4 | 2016-08-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:07 | TRO2.1.9 | Industriel | Etage | BUREAU Opérateur Laveuse | STATION DE LAVAGE CONTAINERS SECOURUE | TRO2.1.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 21:19 | F3A10.17.21.2 | Industriel | Etage |  | PA1155 | F3A10.17.21.2 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:09 | F3A10.17.21.9 | Industriel | Etage |  | PA1151 | F3A10.17.21.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:32 | F3A10.17.21.1 | Industriel | Etage |  | PA1162 | F3A10.17.21.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:33 | F3A10.17.21.1 | Industriel | Etage |  | PA1162 | F3A10.17.21.1 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:34 | F3A10.17.21.3 | Industriel | Etage |  | PA1153 | F3A10.17.21.3 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:36 | F3A10.17.21.7 | Industriel | Etage |  | PA1159 | F3A10.17.21.7 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:39 | F2A8.9 | Industriel | Etage |  | PA1140 | F2A8.9 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:43 | F3A10.19 | Industriel | Etage |  | FLUX LAMINAIRE BOX N° 4 | F3A10.19 | 2016-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:45 | F3D9.4 | Industriel | Etage | face mireuse EISAI 2 | ATELIER BOX 6 DEPAKINE | F3D9.4 | 2017-09-21 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-21 22:51 | F2A8.1.9 | Industriel | Etage | COULOIR DEPAKINE SUD | PA1307 | F2A8.1.9 | 2017-09-21 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-21
MARTIN | Jean-Claude |  |  |  | 2017-09-22 16:40 | PA1129 | Industriel | Etage | STOCKAGE CONTENEUR | PA1129 | PA1129 | 2016-10-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | Pas de repere de provenance d'alimentation | [9 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 16:44 | F3A20.13.24 | Industriel | Etage | STOCKAGE PROVISOIRE LIPANOR | Coffret PA1114 | F3A20.13.24 | 2016-07-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:03 | TRO3.1 | Industriel | Etage | magasin | ARM. DISTRIBUTION P.C. BUREAUX | TRO3.1 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | Mettre les plans dans l'armoire | [9 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:12 | F2A8 | Industriel | Etage | Magasin | ARM. DISTRIBUTION COURANT FORT | F2A8 | 2016-09-22 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | voyant h.s. | 2eme porte n'est pas relié à la terre | [7 empty] | Changé le voyant par 1 ZBV-M1 et relié la porte de gauche à la terre | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:21 | E2A3 | Industriel | Etage | ZT OUEST | Éclairage liquide | E2A3 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | La porte de gauche n'est pas relié à la terre | Des fils non raccordé a mettre dans wagos | [7 empty] | Mettre la porte gauche à la terre et isolé les fils non raccordé | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:28 | F2A8.1.15 | Industriel | Etage | NERI | PA1104 | F2A8.1.15 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 18:39 | F2A8.1.16 | Industriel | Etage | EISAI 2 | PA1252 | F2A8.1.16 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 19:03 | TRA1.3.4 | Industriel | Etage | couloir injectable etage | clim salle info ?? | TRA1.3.4 | 2017-09-22 | NOK | MOYEN | OK | OK | OK | OK | OK | NOK | NOK | [7 empty] | ARMOIRE HORS TENSION | [9 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:16 | F3A20.13.5 | Industriel | Etage | MISE EN GELLULE | GELLULEUSE LIPANOR | F3A20.13.5 | 2017-09-22 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | juste un boîtier de coupure a proximité | [9 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:24 | F3A10.15 | Industriel | Etage | LT SUD LIPANOR | TRAITEMENT AIR PMA 800 | F3A10.15 | 2017-09-22 | NOK | OBSOLETE | [14 empty] | ARMOIRE NON TROUVÉ PROBABLEMENT SUPPRIMER | [9 empty] | NOK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:26 | F3A19 | Industriel | Rdc | TRAVEE D | Machinerie mc2 | F3A19 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:30 | TRO2.4.6 | Industriel | etage | bureaux injectable etage locl fournitures |  | TRO2.4.6 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:33 | TRO2.4.6 | Industriel | etage | bureaux injectable etage locl fournitures |  | TRO2.4.6 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:37 | F2A8BIS.9 | Industriel | Etage | Couloir centrale porte magasin | PA1260 | F2A8BIS.9 | 2017-09-22 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:40 | F2A8BIS9 | Industriel | Etage | Couloir central Porte magasin | PA1225 | F2A8BIS9 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | [17 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:43 | TRO3.1.9 | Industriel | Etage | COTE MC4 | ZT INJECTABLE GTC | TRO3.1.9 | 2016-09-22 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:45 | F2A5 | Industriel | Etage | Couloire près MC 4 | CTA mirage | F2A5 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:47 | F3A17 | Industriel | Etage | ZT SUD couloir | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:50 | F2A8.1.9 | Industriel | Etage | COULOIR DEPAKINE SUD | PA1306 | F2A8.1.9 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-22 20:55 | F2A8.1.7 | Industriel | Etage | EISAI3 MIREUSE | PA1197 | F2A8.1.7 | 2016-09-22 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Le même départ alimente la porte 1198 | [9 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:27 | TRO3.24 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.24 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:31 | TRO3.3 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.3 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26
MARTIN | Jean-Claude |  |  |  | 2017-09-26 11:34 | E4A9 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A9 | 2016-09-26 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-26
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:27 | TRO3.24 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.24 | 2016-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:38 | E4A13 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A13 | 2016-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 08:40 | TRO3.23 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.23 | 2016-09-27 | OK | BON | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 16:43 | ?4 | Industriel | etage cote nord |  | ligne de manutention de charges palettisees | ? | 2017-09-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 16:47 | E1B5.12.1.5 | Industriel | Etage |  | PA1103 | E1B5.12.1.5 | 2017-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:27 | ?5 | Industriel | etage cote nord |  | PA1053 | ? | 2017-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:30 | E1B5.D13 | Industriel | Etage |  | PA1259 | E1B5.D13 | 2016-06-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:36 | F1A3.3 | Industriel | Etage | ESCALIER PRES MC3 - POTEAU 20B | AEROTHERMES RECEPTION EXPEDITION MP | F1A3.3 | 2016-07-27 | OK | BON |  | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | D2 consigne ,aerotherme Z1.3 | [9 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:39 | F1A17.15 | Industriel | Etage | CLIMATISEUR MAGASIN | Traitement d'air magasin reception AC | F1A17.15 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 17:45 | E1B5 | Industriel | Etage | Près MC 3 | Éclairage + PC bureaux réception | E1B5 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:06 | TRO3.2.4 | Industriel | Etage | Local Informatique | Coffret TRO3.2.4 | TRO3.2.4 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:15 | ?6 | Industriel | etage |  | cta | F1A17/17 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:18 | F1B10 | Industriel | Etage | Travée A matières premières | CTA Atelier de prelevement | F1B10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:25 | F1A17.19 | Industriel | Etage |  | PA1223 | F1A17.19 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:28 | E1B5.49 | Industriel | Etage |  | PA1125 | E1B5.49 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:30 | F1A17.19 | Industriel | Etage |  | PA1224 + PA1224 | F1A17.19 | 2017-09-27 | OK | BON | [24 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:35 | F3A32.11 | Industriel | etage |  | TA LOCAL DELIVRANCE SUCRE | F3A32.11 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:38 | F3A32.10 | Industriel | Etage |  | PA1199 + PA1200 | F3A32.10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:40 | F3A32.10 | Industriel | Etage |  | PA1199 | F3A32.10 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:48 | ?7 | Industriel | etage nord |  | sonde temperature magasin | tro3.1.11 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | NOK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 18:53 | ?8 | Industriel | etage nord |  | chambre froide 2-8 degres rideaux rapide | f3a32.17 | 2017-09-27 | NOK | BON | SO | OK | OK | OK | OK | NOK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:10 | ?9 | Industriel | etage | rideaux rapide acces Glatt8 | PA | ? | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:20 | ?10 | Industriel | etage | zone technique glatt8 | coffret electrique Fike 6PE _1_1 | ? | 2017-09-27 | NOK | BON | SO | NOK | OK | OK | OK | NOK | NOK | SO | OK | NOK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:24 | ?11 | Industriel | etage | local technique glatt 8 | armoire contrôle commande système 11EL_1_1 | tro3.29.10 |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:29 | ?12 | Industriel | etage | local technique glatt 8 | cta | f8.21.17 d17 |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:32 | ?13 | Industriel | etage | local technique glatt8 | système de contrôle LIE | ? |  | NOK | BON | SO | NOK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-27 19:36 | F8A21.17 | Industriel | ETAGE | Zone technique | cta process glatt8 | F8A21.17 |  | NOK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:44 | F3A10.16 | Industriel | Etage | au dessus box de pesée | box peseée 5 | F3A10.16 | 2017-09-29 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:54 | F3A10.19 | Industriel | Etage | Au dessus Box 4 | FLUX LAMINAIRE BOX N° 4 | F3A10.19 | 2016-09-29 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29
MARTIN | Jean-Claude |  |  |  | 2017-09-29 12:58 | F3A10.35 | Industriel | Etage | Au dessus du BOX 2 | BOX2 | F3A10.35 | 2016-09-29 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-29
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:25 | F3A17 | Industriel | Etage | ZT SUD | PC 63A ETAGE ( sur IPN du Bardage ) | F3A17 | 2016-09-22 | OK | BON | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-09-22
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:29 | F3A32.14 | Industriel | Etage | STOKAGE | TRAITEMENT D'AIRE CM1042 | F3A32.14 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | OK | OK | SO | OK | OK | OK | NOK | OK | OK | serrure legrand absent | [9 empty] | OK | 2017-09-27
MARTIN | Jean-Claude |  |  |  | 2017-10-02 20:30 | ?14 | Industriel | cote nord | bureaux local informatique |  | E1B5.40 | 2016-09-27 | OK | BON | SO | OK | OK | OK | OK | NOK | NOK | SO | OK | OK | OK | OK | OK | OK | pas de plan | [9 empty] | OK | 2017-09-27

## OCTOBRE
Nom | Prénom | Direction Déléguée | GID (identifiant INEO) | information supplémentaire | Date de réponse | Sélectionner l'armoire concernée | Bâtiment | Niveau | Local | Nom (si précisé) | Numéro de l'Armoire | Date de la dernière pastille / de l'année précédente | PASTILLE PRESENTE | ETAT GENERAL | DISJONCTEUR CONSIGNE - FV | IMPLANTATION - FO | CONTROLE DES VOYANTS - FO | PROPRETE - FO | SORTIES DE CABLES - FO | PLANS PRESENTS - FO | PLANS A JOUR - FO | ECHAUFFEMENT - FR | VENTILATION - FR | IDENTIFICATION DE L'ARMOIRE - FR | VERIFICATION DES PROTECTIONS CONTRE LES CONTACTS DIRECTS - FR | FERMETURE / PORTE - FR | MISE A LA TERRE (CHASSIS/PORTE) - FR | ACCESSIBILITE - FR | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire 4 | Commentaire 5 | Commentaire 6 | Commentaire 1 | Commentaire 2 | Commentaire 3 | Commentaire | NOUVELLE VIGNETTE COLLEE SUR L'ARMOIRE | Date du contrôle
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:35 | F4A9 | Administratif | ETAGE | CUISINE DIRECTION | TD CUISINE DIRECTION | F4A9 | 2016-09-04 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | vérifier si la consignation datant depuis 2013 est toujours d'actualité | relier la porte a la terre | [8 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:42 | E4A10 | Administratif | Etage | COULOIR DIRECTION | eclairage+PC direction | E4A10 | 2016-09-04 | OK | BON | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-04 18:46 | TRO3.5 | Administratif | ETAGE | COULOIR DIRECTION | PC ONDULE | TRO3.5 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:02 | F4A9.7 | Administratif | ETAGE | SALLE REUNION DIRECTION MEZZ 1 | TD ZONE | F4A9.7 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:08 | E4A12 | Administratif | Etage | COULOIR BAT ADMIN | Éclairage + PC | E4A12 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-04 19:11 | TRO3.22 | Administratif | Etage | COULOIR BAT ADMIN | PC ONDULE | TRO3.22 | 2016-09-04 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-04
MARTIN | Jean-Claude |  |  |  | 2017-10-05 20:49 | F7A11.13.1 | Platine | Etage | ZT SUD | FLUX LUMINAIRES WEISS | F7A11.13.1 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:04 | TRO4.1.2 | Platine | Etage | Technique EST | TD ONDULE R+1 REP12 | TRO4.1.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | mettre les plans à jour | [9 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:08 | F7A11 | Platine | ETAGE | Zone technique étage Sud-Est | TD R+1-3 REP15 | F7A11 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:11 | F7A11.12 | Platine | Etage | Technique EST | MELANGEUR VRIECO PLAVIX | F7A11.12 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:19 | F7A11.13.2 | Platine | Etage | Technique EST | CALIBREUR + POMPE A POUDRE E37 | F7A11.13.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:21 | F7A11.13.3 | Platine | Etage | Technique EST | CALIBREUR CLOPI LOCAL e33 + COMPACTAGE r32 | F7A11.13.3 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:25 | F7A11.13.4 | Platine | ETAGE | LT E81 | CALIBRAGE OSCILLANT FREWIT CLOPI E3 | F7A11.13.4 | 2016-09-05 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Armoire consignés depuis 2007 | [9 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:32 | F7A11.13.4.D9 | Platine | Etage | Zone technique EST | Mat GERBEURS | F7A11.13.4.D9 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Armoire hors tension équipement désengager | [9 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:35 | F7A11.13.3.D21 | Platine | Etage | Technique EST | MAT ROTATIF | F7A11.13.3.D21 | 2016-09-05 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Voyant sous tension a changer | [9 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 21:46 | F7A11.13.2.D21 | Platine | Etage | Technique EST | COFFRET MAT ROTATIF | F7A11.13.2.D21 | 2016-09-05 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Q3 consignés | Remplacé le voyant sous tension 24v | [8 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:44 | F3A10.18 | Industriel | Etage |  | FLUX LAMINAIRE BOX N° 3 | F3A10.18 | 2016-09-02 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | [10 empty] | OK | 2017-10-02
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:46 | TRO4.1.2 | Platine | Etage | Technique EST | TD ONDULE R+1 REP12 | TRO4.1.2 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:47 | F7A10.13.5 | Platine | Etage | ZONE TECHNIQUE SUD | table elevatrice aprovel | F7A10.13.5 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:48 | F7A10.13.1 | Platine | Etage | ZONE TECHNIQUE SUD | DEPOTAGE CALIBRAGE IRBESARTAN | F7A10.13.1 | 2016-09-05 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-05 22:50 | F7A10.13.1.D21 | Platine | Etage | ZONE TECHNIQUE SUD | Mat Rotative | F7A10.13.1.D21 | 2016-09-05 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-05
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:25 | F7A10.13.1 | Platine | Etage | ZONE TECHNIQUE SUD | DEPOTAGE CALIBRAGE IRBESARTAN | F7A10.13.1 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:35 | F7A21.1 | Platine | Etage | ZONE TECHNIQUE SUD | CTA PLAVIX | F7A21.1 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:41 | F7A21 | Platine | Etage | ZONE TECHNIQUE SUD | ARMOIRE DISTRIBUTION CTA + DEPOUSSIEREUR | F7A21 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:46 | F7A10 | Platine | ETAGE | Zone technique étage .SUD | ARMOIRE DISTRIBUTION | F7A10 | 2016-09-06 | OK | BON | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | F7A10.8 Consignés (alim sirène porte) | [9 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 18:54 | F7A21.2 | Platine | Etage | ZT SUD | CTA1.1 | F7A21.2 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:11 | F7A18.D3 | Platine | Etage | ZONE Technique SUD Local Dpoussieureures D3 D4 | DEPOUSSIEUR UD3 1083 | F7A18.D3 | 2016-10-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | [15 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:28 | F7A21.3 | Platine | Etage | ZONE TECHNIQUE SUD | CTA | F7A21.3 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [11 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:29 | F7A21.6 | Platine | ETAGE | LT E80 E80.7 | DEPOUSSIEREURE D7 | F7A21.6 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:30 | F7A21.5 | Platine | ETAGE | LT E80 E80.3 | depousierreur D6 | F7A21.5 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:31 | F7A21.4 | Platine | ETAGE | LT E80 E80.1 | depoussierreur D5 | F7A21.4 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | NOK | SO | OK | OK | OK | OK | OK | OK | OK | Mettre les plans dans l'armoire | [9 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:34 | F7A10.13.2.D21 | Platine | Etage | ZONE TECHNIQUE SUD | MAT ROTATIF | F7A10.13.2.D21 | 2016-09-06 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | Changer le voyant sous tension | [9 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-06 19:47 | TRO4.1.2.12 | Platine | Etage | Zone technique SUD | ZT-R81-GTC | TRO4.1.2.12 | 2016-09-06 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-06
MARTIN | Jean-Claude |  |  |  | 2017-10-16 17:58 | F3A32.11 | Industriel | etage |  | TA LOCAL DELIVRANCE SUCRE | F3A32.11 | 2017-10-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 18:02 | F3A32.10 | Industriel | Etage |  | PA1200 | F3A32.10 | 2017-10-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 19:38 | F8A21.17 | Industriel | ETAGE | Zone technique ouest | TD chargeur | F8A21.17 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | il faut fermer les ouvertures dans le plastron du bas | [9 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 19:41 | F8A21.9 | Industriel | Etage | ZT Ouest | CTA GRAB 2B, LOCAL CHARGE, BUREAUX | F8A21.9 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 20:12 | F8A20 | Industriel | Etage | ZT OUEST | ZONE TECHNIQUE ETAGE FONCTIONS SUPPORT | F8A20 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 20:17 | F8A20.3 | Industriel | Etage | ZT FONCTIONS SUPPORT | CTA GELLULEUSES 1 & 2 | F8A20.3 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:21 | F8A16.6.1 | Industriel | Etage | Local delivrance sucre | CE1001 | F8A16.6.1 | 2016-07-16 | OK | MOYEN | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:38 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:39 | F1A17.12 | Industriel | Etage | CENTRALE PRELEVEMENT | CENTRALE PRELEVEMENT | F1A17.12 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:54 | F1A17.5 | Industriel | Etage | Box prelevement 2 | Box prelevement 2 | F1A17.5 | 2016-09-16 | OK | BON | OK | OK | NOK | OK | OK | OK | OK | OK | NOK | OK | OK | OK | OK | OK | voir a changer le ventilateur | changer le voyant sous tension | [8 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 21:57 | F1A17.2 | Industriel | Etage | Box prelevement 3 | Box prelevement 3 | F1A17.2 | 2016-09-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:15 | F1A17.21.3 | Industriel | Etage | QUAI NORD | PA1102 | F1A17.21.3 | 2016-07-16 | OK | MOYEN | OK | OK | OK | OK | OK | NOK | NOK | OK | OK | OK | OK | OK | OK | OK | Il faut mettre les plans dans le coffret | [9 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:21 | F1A17.15 | Industriel | Etage | CLIMATISEUR MAGASIN | Traitement d'air magasin reception AC | F1A17.15 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:23 | F1A3.3 | Industriel | Etage | ESCALIER PRES MC3 - POTEAU 20B | AEROTHERMES RECEPTION EXPEDITION MP | F1A3.3 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-16 22:25 | E1B5 | Industriel | Etage | Près MC 3 | Éclairage + PC bureaux réception | E1B5 | 2016-07-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-18 22:30 | F1B10 | Industriel | Etage | Travée A matières premières | CTA Atelier de prelevement | F1B10 | 2016-08-16 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-16
MARTIN | Jean-Claude |  |  |  | 2017-10-18 22:37 | F1A17.17 | Industriel | Etage | RECEPTION MP | PA2082 | F1A17.17 | 2016-09-18 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-18
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:27 | F7A9 | Platine | Etage | Zone technique étage .NORD EST | TD R+1-1 REP13 | F7A9 | 2016-09-19 | OK | BON | NOK | OK | NOK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | DT40 F7A9.14.4 Alim porte tirette sud coupé avec un cadenas numero 8 | Refaire la cosse de terre sur la porte | Voynt sur la porte non raccorde6 | [7 empty] | OK | 2017-10-19
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:31 | F7A9.14.3 | Platine | Etage | magasin Platine | PA 2024 | F7A9.14.3 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:37 | F7A9.14.2 | Platine | Etage | magasin Platine | PA 2023 | F7A9.14.2 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 17:47 | TRO4.1.2.4 | Platine | Etage | Magasin | Yokogawa température | TRO4.1.2.4 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | [11 empty] | OK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 18:28 | F7A11.13.7 | Platine | ETAGE | Stockage MATERIEL | TDE92 | F7A11.13.7 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | Il faut dégagée devant l'armoire | [9 empty] | OK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 18:44 | F7A11.7 | Platine | ETAGE | ENTREE PLATINE | COFFRET VENTOUSE | F7A11.7 | 2017-10-20 | NOK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | Coffret très haut il faut l'échelle pour y accéder | [9 empty] | NOK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 21:30 | E1B5.49 | Industriel | Etage |  | PA1125 | E1B5.49 | 2017-10-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | [10 empty] | OK | 2017-10-20
MARTIN | Jean-Claude |  |  |  | 2017-10-20 21:34 | F3A32.14 | Industriel | Etage | STOKAGE | TRAITEMENT D'AIRE | F3A32.14 | 2016-09-20 | OK | BON | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | NOK | OK | OK | manque serrure | [9 empty] | OK | 2017-10-20